## DATA_DICTIONARY
DATA DICTIONARY - PROCESS MASTER DATA
1. SHEET RELATIONSHIPS
Sheet Name | Type | Description
INPUT_DATA | Master sheet | Contains all stream process data (flow, pressure, temp, etc.)
LIST_OF_EQUIPMENT | Dependent | References INPUT_DATA for operating conditions and fluid connections
LIST OF LINES | Dependent | References INPUT_DATA for sizing; Uses Pipe Table for selection
LIST OF INSTRUMENTS | Dependent | References LIST OF LINES and INPUT_DATA for process conditions
LIST OF VALVES | Dependent | References LIST OF LINES and INPUT_DATA for process conditions
Pipe Table | Reference | Static lookup table for Schedule 40 pipe dimensions
2. NAMED RANGES
Named Range | Sheet | Range | Description
StreamData | INPUT_DATA | $A$4:$J$195 | All stream process data
LineTags | INPUT_DATA | $A$4:$A$195 | Line tag identifiers (primary key)
FlowRates_kgs | INPUT_DATA | $C$4:$C$195 | Flow rates in kg/s
FlowRates_kghr | INPUT_DATA | $D$4:$D$195 | Flow rates in kg/hr
Pressures_mbar | INPUT_DATA | $E$4:$E$195 | Pressures in mbar (absolute)
Pressures_bar | INPUT_DATA | $F$4:$F$195 | Pressures in bar (absolute)
Temperatures | INPUT_DATA | $G$4:$G$195 | Temperatures in °C
Densities | INPUT_DATA | $H$4:$H$195 | Densities in kg/m³
TDS_Values | INPUT_DATA | $I$4:$I$195 | Total Dissolved Solids in ppm
Enthalpies | INPUT_DATA | $J$4:$J$195 | Enthalpy in kJ/kg
PipeReference | Pipe Table | $A$2:$E$19 | Pipe sizing lookup table
PipeIDs | Pipe Table | $A$2:$B$19 | Pipe inner diameter ranges
EquipmentTags | LIST_OF_EQUIPMENT | $B$3:$B$31 | Equipment tag numbers
LineNumbers | LIST OF LINES | $B$4:$B$214 | Line numbers for validation
3. FLUID CATEGORIES
Category | Tag Range | Description
SEA WATER | SW1 - SW17 | Incoming seawater streams
BRINE WATER | B1 - B23 | Concentrated brine streams
DISTILLATE WATER | D1 - D25 | Product distillate streams
STEAM | ST1 - ST16 | Steam and vapor streams
NCG | NCG1 - NCG12 | Non-condensable gas streams
FEED WATER | FW1 - FW95 | Feed water streams to effects
4. FORMULA PATTERNS (for reference)
Purpose | Formula Pattern | Notes
Lookup Pressure |  | Get pressure by line tag
Lookup Flow |  | Get flow rate by line tag
Lookup Temperature |  | Get temperature by line tag
Lookup Density |  | Get density by line tag
Pipe Size Selection | Check | Select pipe from calculated ID
5. DATA VALIDATION RULES
Sheet | Field | Validation Type
LIST OF LINES | Column D (Input Data) | Dropdown from LineTags
LIST OF INSTRUMENTS | Column C (Line No.) | Dropdown from LineNumbers
LIST OF INSTRUMENTS | Column H (Fluid) | Dropdown from fluid categories
LIST OF VALVES | Column C (Line Number) | Dropdown from LineNumbers
LIST OF VALVES | Column I (Fluid) | Dropdown from fluid categories
LIST_OF_EQUIPMENT | Columns E-M (Fluids) | Dropdown from LineTags
6. LOOKUP CHAIN FOR INSTRUMENTS
LIST OF INSTRUMENTS.Line No (Col C) | → LIST OF LINES.Line No (Col B) → Line Tag (Col D) | → INPUT_DATA.Line Tag (Col A) → Values

## INPUT_DATA
Line Tag | Description | Flow Rate | Flow Rate | Pressure | Pressure | Temperature | Density | TDS | Enthalpy (Ref: Pure Water, 0 C, 1 atm) | NOTE: This sheet is the Master Data source
Unit |  | kg/s | kg/hr | mbar (a) | bar a | °C | kg/m³ | ppm | kJ/kg | Named ranges defined: LineTags, FlowRates_kgs, Pressures_bar, etc.
SEA WATER | [9 empty] | See DATA_DICTIONARY sheet for full documentation
SW1 |  | 32.0895 | 115522.2143 | 1000 | 1 | 30 | 1026.3219 | 39504.4316 | 448.4402
SW2 |  | 32.0895 | 115522.2143 | 3500 | 3.5 | 30.0862 | 1026.408 | 39504.4316 | 448.7821
SW3 |  | 11.19 | 40284 | 3500 | 3.5 | 30.0863 | 1026.41 | 39504.4316 | 448.7826
SW4 |  | 11.1895 | 40282.2143 | 3500 | 3.5 | 36 | 1024.39 | 39504.4316 | 448.7826
SW5 |  | 3.7298 | 13427.4048 | 3500 | 3.5 | 36 | 1024.39 | 39504.4316 | 448.7826
SW6 |  | 3.7298 | 13427.4048 | 3500 | 3.5 | 36 | 1024.39 | 39504.4316 | 448.7826
SW7 |  | 3.7298 | 13427.4048 | 3500 | 3.5 | 36 | 1024.39 | 39504.4316 | 448.7826
SW8 |  | 9.9 | 35640 | 3500 | 3.5 | 30.09 | 1024.39 | 39504.4316 | 474.0602
SW9 |  | 9.9 | 35640 | 3500 | 3.5 | 36.45 | 1026.41 | 39504.4316 | 474.0602
SW10 |  | 3.3 | 11880 | 3500 | 3.5 | 36.45 | 1026.41 | 39504.4316 | 474.0602
SW11 |  | 3.3 | 11880 | 3500 | 3.5 | 36.45 | 1026.41 | 39504.4316 | 474.0602
SW12 |  | 3.3 | 11880 | 3500 | 3.5 | 36.45 | 1026.41 | 39504.4316 | 474.0602
SW13 |  | 11 | 39600 | 3500 | 3.5 | 30.0863 | 1024.2273 | 39504.4316 | 472.2519
SW14 |  | 11 | 39600 | 3500 | 3.5 | 33.9094 | 1026.408 | 39504.4316 | 463.963
SW15 |  | 3.6667 | 13200 | 3500 | 3.5 | 33.9094 | 1026.408 | 39504.4316 | 463.963
SW16 |  | 3.6667 | 13200 | 3500 | 3.5 | 33.9094 | 1026.408 | 39504.4316 | 463.963
SW17 |  | 3.6667 | 13200 | 3500 | 3.5 | 33.9094 | 1026.408 | 39504.4316 | 463.963
BRINE WATER
B1 | Siphon 1 | 4.07 | 14652 | 259.4 |  | 66.55 | 1043.56 | 63600 | 785.3251
B2 | Siphon 2 | 8.33 | 29988 | 219.6 |  | 62.81 | 1042.53 | 62100 | 758.9935
B3 | Siphon 3 | 12.73 | 45828 | 188 |  | 59.4 | 1041.71 | 60900 | 736.6451
B4 | Siphon 4 | 17.26 | 62136 | 161.8 |  | 56.2 | 1041.51 | 60600 | 721.7469
B5 | Siphon 5 | 21.81 | 78516 | 139.5 |  | 53.1 | 1041.37 | 60400 | 707.6334
B6 | Siphon 6 | 26.34 | 94824 | 119.8 |  | 50 | 1041.3 | 60300 | 694.7095
B7 | Siphon 7 | 31.02 | 111672 | 101.7 |  | 46.72 | 1041.16 | 60100 | 680.4478
B8 | Siphon 8 | 35.55 | 127980 | 94.6 |  | 43.14 | 1041.23 | 60200 | 667.4554
B9 | To brine tank | 39.83 | 143388 | 68 |  | 39 | 1041.51 | 60600 | 655.1861
B10 | Brine tank to Brine pump skid | 39.8335 | 143400.6516 | 2500 | 2.5 | 39.071 | 1039.7242 | 60600 | 655.4602
B11 |  | HOLD | #VALUE! | 2500 | 2.5 | 37.4474 | 1040.3579 |  | 649.1781
B12 |  | HOLD | #VALUE! | 2500 | 2.5 | 37.4474 | 1040.3579 |  | 649.1781
B13 |  | 18.925 | 68130 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
B14 |  | 18.925 | 68130 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
B15 | EFF-1 | 1.84 | 6624 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
B16 | EFF-2 | 1.84 | 6624 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
B17 | EFF-3 | 1.83 | 6588 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
B18 | EFF-4 | 2.31 | 8316 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
B19 | EFF-5 | 2.31 | 8316 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
B20 | EFF-6 | 2.31 | 8316 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
B21 | EFF-7 | 2.16 | 7776 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
B22 | EFF-8 | 2.16 | 7776 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
B23 | EFF-9 | 2.16 | 7776 | 2500 | 2.5 | 37.4474 | 1040.3579 | 60600 | 649.1781
DISTILLATE WATER
D1 |  | 1.88 | 6768 | 320.5 |  | 70.59 | 988.028 | NIL | 412.8
D2 |  | 3.38 | 12168 | 259.4 |  | 65.74 | 989.708 | NIL | 331.6
D3 |  | 4.68 | 16848 | 219.6 |  | 62.02 | 990.911 | NIL | 295.7
D4 |  | 5.84 | 21024 | 188 |  | 58.62 | 991.945 | NIL | 271.7
D5 |  | 6.93 | 24948 | 161.8 |  | 55.43 | 992.858 | NIL | 253
D6 |  | 7.98 | 28728 | 139.5 |  | 52.33 | 993.693 | NIL | 237.1
D7 |  | 9.06 | 32616 | 119.8 |  | 49.23 | 994.476 | NIL | 222.6
D8 |  | 10.21 | 36756 | 101.7 |  | 45.97 | 995.244 | NIL | 208.2
D9 |  | 11.51 | 41436 | 84.6 |  | 42.4045 | 996.019 | NIL | 193.3188
D10 |  | 11.58 | 41688 | 1500 | 1.5 | 42.4936 | 991.334 | NIL | 177.8697
D11 |  | 11.58 | 41688 |  |  | 42.4936 | 991.334 | NIL | 177.8697
D12 |  | 11.58 | 41688 |  |  |  | 991.334 | NIL | 177.8697
D13 | INITIAL FILL UP IN | 6.94 | 24984 |  |  | 30 | 996.019 |  | 125.91
D14 | MAKE UP | 0.46822 | 1685.5898 |  |  | 30 | 996.019 |  | 154.8601
D15 | INITIAL FILL UP OUT | 0.611 | 2199.6 |  |  | 30 | 996.019 |  | 154.8601
D16 |  | 0.04 | 144 |  |  | 30 | 993.4479 |  | 154.8601
D17 |  | 0.28822 | 1037.5898 | 1500 | 1.5 | 36.9869 | 993.4479 | NIL | 154.8601
D18 | DS-SUPER HEATER | 0.14 | 504 |  |  | 30 | 996.019 |  | 154.8601
D19 |  | 6.2463 | 22500 | 1100 |  | 65 | 980.5187 | NIL | 272.0029
D20 |  | 5.958 | 21456 | 68 |  | 38.39 | 992.8687 | NIL | 160.7174
D21 |  | 5.958 | 21448.9159 | 68 |  | 38.33 |  | NIL | #VALUE!
D22 |  | 3.1 | 11160 | 1200 |  | 78 | 972.9238 | NIL | 326.4893
D23 |  | 3.0588 | 11016 | 320.5 |  | 70 | 977.3215 | NIL | 295.4607
D24 |  | 4.5588 | 16411.8047 | 320.5 |  | 69.56 |  | NIL | #REF!
D25 | FC - Distillate Outlet | 0.070788 | 254.837 | 67.97 | 0.06797 | 34.9098 | 994.1208 | NIL | 146.1819
STEAM
S1 |  | 1.5 | 5400 | 259.4 |  | 66.55 | 0.16317 | NIL | 2625.3696
S2 |  | 1.3 | 4680 | 219.6 |  | 62.81 | 0.13921 | NIL | 2618.5701
S3 |  | 1.16 | 4176 | 188 |  | 59.4 | 0.12016 | NIL | 2612.3605
S4 |  | 1.08 | 3888 | 161.8 |  | 56.2 | 0.10435 | NIL | 2606.3946
S5 |  | 1.06 | 3816 | 139.5 |  | 53.1 | 0.09086 | NIL | 2600.6747
S6 |  | 1.08 | 3888 | 119.8 |  | 50 | 0.07892 | NIL | 2594.9064
S7 |  | 1.15 | 4140 | 101.7 |  | 46.72 | 0.06791 | NIL | 2588.8576
S8 |  | 1.3 | 4680 | 84.6 |  | 43.14 | 0.05745 | NIL | 2582.1079
S9 |  | 1.84 | 6624 | 68 |  | 39 | 0.04722 | NIL | 2574.2868
S10 | MVC-1 OUTLET
S11 | MVC-2 OUTLET
S12 | MVC-3 OUTLET
S13 | S10 ADDED IN S9 | 0.29 | 1044 | 67.9695 | 0.067969 | 38.3888 | 0.047309 | NIL | 2572.4816
S14 |  | 0.041165 | 148.1953 | 320.4559 | 0.32046 | 70.6 | 0.20256 | NIL | 2632.0969
SM | HTFV + MVC-3 OUTLET | 1.879 | 6764.4 | 320.46 | 0.32046 | 70.6 | 0.20256 | NIL | 2632.6397
NON CONDENSABLE GAS
NCG1 |  | 0.00012614 | 0.4541 | 320 |  | 36.5 | 0.3286
NCG2 |  | 0.00025681 | 0.9245 | 259 |  | 36.5 | 0.25988
NCG3 |  | 0.00039786 | 1.4323 | 219 |  | 36.5 | 0.21216
NCG4 |  | 0.00055731 | 2.0063 | 187 |  | 36.9 | 0.18041
NCG5 |  | 0.00073814 | 2.6573 | 161 |  | 36.9 | 0.15148
NCG6 |  | 0.00095906 | 3.4526 | 138 |  | 36.9 | 0.12632
NCG7 |  | 0.001181 | 4.2515 | 119 |  | 35.7 | 0.10741
NCG8 |  | 0.0057625 | 20.745 | 100 |  | 44.01 | 0.072102
NCG9 |  | 0.032908 | 118.47 | 82 |  | 41.91 | 0.056642
NCG10
NCG11 | LRVP INLET
NCG12 | LRVP OUTLET
FEED WATER
F1 |  | 5.5698 | 20051.4048 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F1.1 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F1.2 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F1.3 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F1.4 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F1.5 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F1.6 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F1.7 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F1.8 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F1.9 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F1.10 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2 |  | 5.5698 | 20051.4048 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2.1 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2.2 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2.3 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2.4 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2.5 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2.6 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2.7 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2.8 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2.9 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F2.10 |  | 0.55698 | 2005.1405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3 |  | 5.5598 | 20015.4048 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3.1 |  | 0.55598 | 2001.5405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3.2 |  | 0.55598 | 2001.5405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3.3 |  | 0.55598 | 2001.5405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3.4 |  | 0.55598 | 2001.5405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3.5 |  | 0.55598 | 2001.5405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3.6 |  | 0.55598 | 2001.5405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3.7 |  | 0.55598 | 2001.5405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3.8 |  | 0.55598 | 2001.5405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3.9 |  | 0.55598 | 2001.5405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F3.10 |  | 0.55598 | 2001.5405 | 2500 |  | 36.46 | 1029.6111 | 46470.8339 | 530.593
F4 |  | 5.61 | 20196 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F4.1 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F4.2 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F4.3 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F4.4 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F4.5 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F4.6 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F4.7 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F4.8 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F4.9 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F4.10 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5 |  | 5.61 | 20196 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5.1 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5.2 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5.3 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5.4 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5.5 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5.6 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5.7 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5.8 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5.9 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F5.10 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6 |  | 5.61 | 20196 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6.1 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6.2 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6.3 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6.4 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6.5 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6.6 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6.7 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6.8 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6.9 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F6.10 |  | 0.561 | 2019.6 | 2500 |  | 36.85 | 1030.8208 | 48203.5224 | 546.1675
F7 |  | 5.8267 | 20976 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F7.1 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F7.2 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F7.3 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F7.4 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F7.5 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F7.6 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F7.7 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F7.8 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F7.9 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F7.10 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8 |  | 5.8267 | 20976 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8.1 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8.2 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8.3 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8.4 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8.5 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8.6 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8.7 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8.8 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8.9 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F8.10 |  | 0.58267 | 2097.6 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F9 |  | 5.8267 | 20976 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F9.1 |  | 0.97111 | 3496 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F9.2 |  | 0.97111 | 3496 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F9.3 |  | 0.97111 | 3496 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F9.4 |  | 0.97111 | 3496 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F9.5 |  | 0.97111 | 3496 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951
F9.6 |  | 0.97111 | 3496 | 2500 |  | 35.2 | 1030.7582 | 47344.36 | 532.6951

## LIST_OF_EQUIPMENT
Equipment Name | Equipment Tag No. | Operating Pressure | Operating Temperature | Fluid_In_1 | Fluid_In_2 | Fluid_In_3 | Fluid_In_4 | Fluid_In_5 | Fluid_Out_1 | Fluid_Out_2 | Fluid_Out_3 | Fluid_Out_4
Units |  | mbar (a) | °C
Low Temperature Flash Vessel | LTFV | 67.9695 | 38.3888 | D19 |  |  |  |  | D20 | S13
High Temperature Flash Vessel | HTFV | 320.4559 | 70.6 | D22 |  |  |  |  | D23 | S14
MED Train - 1 | MED - E1 | 320.46 | 70.6 | S13 | S14 | F1 |  |  | B1 | D1 | S1 | NCG1
MED Train - 1 | MED - E2 | 259.4 | 66.55 | S1 | NCG1 | F2 | B1 | D1 | B2 | D2 | S2 | NCG2
MED Train - 1 | MED - E3 | 219.6 | 62.81 | S2 | NCG2 | F3 | B2 | D2 | B3 | D3 | S3 | NCG3
MED Train - 2 | MED - E4 | 188 | 59.4 | S3 | NCG3 | F4 | B3 | D3 | B4 | D4 | S4 | NCG4
MED Train - 2 | MED - E5 | 161.8 | 56.2 | S4 | NCG4 | F5 | B4 | D4 | B5 | D5 | S5 | NCG5
MED Train - 2 | MED - E6 | 139.5 | 53.1 | S5 | NCG5 | F6 | B5 | D5 | B6 | D6 | S6 | NCG6
MED Train - 3 | MED - E7 | 119.8 | 50 | S6 | NCG6 | F7 | B6 | D6 | B7 | D7 | S7 | NCG7
MED Train - 3 | MED - E8 | 101.7 | 46.72 | S7 | NCG7 | F8 | B7 | D7 | B8 | D8 | S8 | NCG8
MED Train - 3 | MED - E9 | 84.6 | 43.14 | S8 | NCG8 | F9 | B8 | D8 | B9 | D9 | S9 | NCG9
Final Condenser | FC | 82 | 41.91 | SW13 | NCG9 |  |  |  | SW14 | NCG10
Brine Plate Heat Exchanger | BPHE |  |  | B10 | SW8 |  |  |  | B11 | SW9
Distillate Plate Heat Exchanger | DPHE |  |  | D11 | SW3 |  |  |  | B12 | SW4
Brine Tank | BT | 68 | 39 | B9 |  |  |  |  | B10
Distillate Tank | DT | 84.6 | 42.4045 | D9 | D25 |  |  |  | D10
Sea Water Pump | SWP |  |  | SW1 |  |  |  |  | SW2
Brine Pump | BP |  |  | B9 |  |  |  |  | B10
Distillate Pump | DP |  |  | D10 |  |  |  |  | D11
Initial Fill Pump | IFP |  |  | D13 |  |  |  |  | D15
Make Up Pump | MP |  |  | D14 |  |  |  |  | D16 | D17 | D18
LTFV-Re Circulation Pump | LTFV-RCP | [7 empty] | D19
HTFV-Re Circulation Pump | HTFV-RCP | [7 empty] | D22
LTFV-Extraction Pump | LTFV-EP |  |  | D21
HTFV-Extraction Pump | LTFV-EP |  |  | D24
Distillate Storage Tank | DST | 0 | 0 | D12 |  |  |  |  | D13 | D14
Anti-Scalant Tank | AST
Anti-Foam Tank | AFT
Acid Cleaning Tank | ACT

## LIST OF LINES
S.No | Line No | Fluid | Input Data | Flow Rate | Density | Calculated Velocity | Calculated Inner diameter | Selected Inner diameter | Actual Velocity
|  |  | Tag No. | kg/s | kg/m3 | m/s | mm | mm | m/s
SEA WATER LINE
1 | 200-40-SS-SW-01 | Sea water | SW1 | 32.0895 | 1026.3219 | 1.6 | 157.7374 | 202.74 | 0.96852
2 | 200-40-SS-SW-02 | Sea water | SW2 | 32.0895 | 1026.408 | 1.6 | 157.7308 | 202.74 | 0.96844
3 | 100-40-SS-SW-03 | Sea water | SW3 | 11.19 | 1026.41 | 2 | 83.3095 | 102.26 | 1.3274
4 | 100-40-SS-SW-04 | Sea water | SW4 | 11.1895 | 1024.39 | 2 | 83.3898 | 102.26 | 1.33
5 | 65-40-SS-SW-05 | Sea water | SW5 | 3.7298 | 1024.39 | 2 | 48.1451 | 52.48 | 1.6832
6 | 65-40-SS-SW-06 | Sea water | SW6 | 3.7298 | 1024.39 | 2 | 48.1451 | 52.48 | 1.6832
7 | 65-40-SS-SW-07 | Sea water | SW7 | 3.7298 | 1024.39 | 2 | 48.1451 | 52.48 | 1.6832
8 | 100-40-SS-SW-08 | Sea water | SW8 | 9.9 | 1024.39 | 2 | 78.4377 | 102.26 | 1.1767
9 | 100-40-SS-SW-09 | Sea water | SW9 | 9.9 | 1026.41 | 2 | 78.3605 | 102.26 | 1.1744
10 | 65-40-SS-SW-10 | Sea water | SW10 | 3.3 | 1026.41 | 2 | 45.2415 | 52.48 | 1.4863
11 | 65-40-SS-SW-11 | Sea water | SW11 | 3.3 | 1026.41 | 2 | 45.2415 | 52.48 | 1.4863
12 | 65-40-SS-SW-12 | Sea water | SW12 | 3.3 | 1026.41 | 2 | 45.2415 | 52.48 | 1.4863
13 | 100-40-SS-SW-13 | Sea water | SW13 | 11 | 1024.2273 | 2 | 82.6872 | 102.26 | 1.3077
14 | 100-40-SS-SW-14 | Sea water | SW14 | 11 | 1026.408 | 2 | 82.5993 | 102.26 | 1.3049
15 | 65-40-SS-SW-15 | Sea water | SW15 | 3.6667 | 1026.408 | 2 | 47.6887 | 52.48 | 1.6515
16 | 65-40-SS-SW-16 | Sea water | SW16 | 3.6667 | 1026.408 | 2 | 47.6887 | 52.48 | 1.6515
17 | 65-40-SS-SW-17 | Sea water | SW17 | 3.6667 | 1026.408 | 2 | 47.6887 | 52.48 | 1.6515
BRINE WATER LINE
18 | 150-40-SS-BW-01 | Brine | B1 | 4.07 | 1043.56 | 0.4 | 111.4201 | 154.08 | 0.20917
19 | 200-40-SS-BW-02 | Brine | B2 | 8.33 | 1042.53 | 0.4 | 159.4789 | 202.74 | 0.24751
20 | 250-40-SS-BW-03 | Brine | B3 | 12.73 | 1041.71 | 0.3 | 227.7379 | 254.56 | 0.24011
21 | 300-40-SS-BW-04 | Brine | B4 | 17.26 | 1041.51 | 0.3 | 265.2059 | 303.64 | 0.22886
22 | 350-40-SS-BW-05 | Brine | B5 | 21.81 | 1041.37 | 0.25 | 326.5956 | 333.34 | 0.23999
23 | 400-40-SS-BW-06 | Brine | B6 | 26.34 | 1041.3 | 0.25 | 358.9261 | 381 | 0.22187
24 | 400-40-SS-BW-07 | Brine | B7 | 31.02 | 1041.16 | 0.3 | 355.5958 | 381 | 0.26133
25 | 450-40-SS-BW-08 | Brine | B8 | 35.55 | 1041.23 | 0.3 | 380.6632 | 428.6 | 0.23665
26 | ID800-8THK-SS-BW-09 | Brine | B9 | 39.83 | 1041.51 | 0.08 | 780.1597 | Plate
27 | ID800-8THK-SS-BW-10 | Brine | B10 | 39.8335 | 1039.7242 | 0.08 | 780.8638 | Plate
28 | XX-XX-SS-BW-11 | Brine | B11 | HOLD | 1040.3579 |  |  | Check Size
29 | 200-40-SS-BW-12 | Brine | B12 | HOLD | 1040.3579 | 1 |  | Check Size
30 | 150-40-SS-BW-13 | Brine | B13 | 18.925 | 1040.3579 | 1.5 | 124.2613 | 154.08 | 0.9756
31 | 150-40-SS-BW-14 | Brine | B14 | 18.925 | 1040.3579 | 1.5 | 124.2613 | 154.08 | 0.9756
32 | 80-40-SS-BW-15 | Brine | B15 | 1.84 | 1040.3579 | 0.5 | 67.1101 | 77.92 | 0.37089
33 | 80-40-SS-BW-16 | Brine | B16 | 1.84 | 1040.3579 | 0.5 | 67.1101 | 77.92 | 0.37089
34 | 80-40-SS-BW-17 | Brine | B17 | 1.83 | 1040.3579 | 0.5 | 66.9274 | 77.92 | 0.36888
35 | 80-40-SS-BW-18 | Brine | B18 | 2.31 | 1040.3579 | 0.7 | 63.5507 | 77.92 | 0.46563
36 | 80-40-SS-BW-19 | Brine | B19 | 2.31 | 1040.3579 | 0.7 | 63.5507 | 77.92 | 0.46563
37 | 80-40-SS-BW-20 | Brine | B20 | 2.31 | 1040.3579 | 0.7 | 63.5507 | 77.92 | 0.46563
38 | 80-40-SS-BW-21 | Brine | B21 | 2.16 | 1040.3579 | 0.7 | 61.4528 | 77.92 | 0.43539
39 | 80-40-SS-BW-22 | Brine | B22 | 2.16 | 1040.3579 | 0.7 | 61.4528 | 77.92 | 0.43539
40 | 80-40-SS-BW-23 | Brine | B23 | 2.16 | 1040.3579 | 0.7 | 61.4528 | 77.92 | 0.43539
DISTILLATE WATER LINE
41 | 100-40-SS-DW-01 | Distillate | D1 | 1.88 | 988.028 | 0.3 | 89.8646 | 102.26 | 0.23168
42 | 150-40-SS-DW-02 | Distillate | D2 | 3.38 | 989.708 | 0.3 | 120.3924 | 154.08 | 0.18316
43 | 150-40-SS-DW-03 | Distillate | D3 | 4.68 | 990.911 | 0.3 | 141.5794 | 154.08 | 0.2533
44 | 200-40-SS-DW-04 | Distillate | D4 | 5.84 | 991.945 | 0.3 | 158.0728 | 202.74 | 0.18237
45 | 200-40-SS-DW-05 | Distillate | D5 | 6.93 | 992.858 | 0.3 | 172.1145 | 202.74 | 0.21621
46 | 200-40-SS-DW-06 | Distillate | D6 | 7.98 | 993.693 | 0.3 | 184.6162 | 202.74 | 0.24876
47 | 200-40-SS-DW-07 | Distillate | D7 | 9.06 | 994.476 | 0.3 | 196.6353 | 202.74 | 0.28221
48 | 250-40-SS-DW-08 | Distillate | D8 | 10.21 | 995.244 | 0.3 | 208.6616 | 254.56 | 0.20157
49 | 450-40-SS-DW-09 | Distillate | D9 | 11.51 | 996.019 | 0.1 | 383.5826 | 428.6 | 0.080096
50 | 450-40-SS-DW-10 | Distillate | D10 | 11.58 | 991.334 | 0.1 | 385.6553 | 428.6 | 0.080964
51 | 100-40-SS-DW-11 | Distillate | D11 | 11.58 | 991.334 | 1.5 | 99.5758 | 102.26 | 1.4223
52 | 100-40-SS-DW-12 | Distillate | D12 | 11.58 | 991.334 | 1.5 | 99.5758 | 102.26 | 1.4223
53 | 100-40-SS-DW-13 | Distillate | D12 | 11.58 | 991.334 | 1.5 | 99.5758 | 102.26 | 1.4223
54 | 100-40-SS-DW-14 | Distillate | D12 | 11.58 | 991.334 | 1.5 | 99.5758 | 102.26 | 1.4223
55 | 100-40-SS-DW-15 | Distillate | D15 | 0.611 | 996.019 | 1.5 | 22.819 | 40.94 | 0.466
56 | 100-40-SS-DW-16 | Distillate | D15 | 0.611 | 996.019 | 1.5 | 22.819 | 40.94 | 0.466
57 | 100-40-SS-DW-17 | Distillate | D15 | 0.611 | 996.019 | 1.5 | 22.819 | 40.94 | 0.466
58 | 100-40-SS-DW-18 | Distillate | D15 | 0.611 | 996.019 | 1.5 | 22.819 | 40.94 | 0.466
59 | 25-40-SS-DW-19 | Distillate | D16 | 0.04 | 993.4479 | 2 | 5.0629 | 15.76 | 0.2064
60 | 25-40-SS-DW-20 | Distillate | D16 | 0.04 | 993.4479 | 2 | 5.0629 | 15.76 | 0.2064
61 | 25-40-SS-DW-21 | Distillate | D16 | 0.04 | 993.4479 | 2 | 5.0629 | 15.76 | 0.2064
62 | 25-40-SS-DW-22 | Distillate | D16 | 0.04 | 993.4479 | 2 | 5.0629 | 15.76 | 0.2064
63 | 300-40-SS-DW-23 | Distillate | D20 | 5.958 | 992.8687 | 0.1 | 276.4143 | 303.64 | 0.082871
64 | 80-40-SS-DW-24 | Distillate | D20 | 5.958 | 992.8687 | 2 | 61.8081 | 77.92 | 1.2584
65 | 80-40-SS-DW-25 | Distillate | D19 | 6.2463 | 980.5187 | 2 | 63.6828 | 77.92 | 1.3359
66 | 15-40-SS-DW-26 | Distillate | D23 | 3.0588 | 977.3215 | 1 | 63.1269 | 77.92 | 0.65634
67 | 15-40-SS-DW-27 | Distillate | D23 | 3.0588 | 977.3215 | 1.5 | 51.5429 | 62.68 | 1.0143
68 | 200-40-SS-DW-28 | Distillate | D24 | 4.5588 | 0 | 0.1 |  | Check Size
69 | 50-40-SS-DW-29 | Distillate | D24 | 4.5588 | 0 | 2 |  | Check Size
70 | 50-40-SS-DW-30 | Distillate | D22 | 3.1 | 972.9238 | 2 | 45.0382 | 52.48 | 1.473
71 | 25-40-SS-DW-31 | Distillate | D18 | 0.14 | 996.019 | 1.5 | 10.9229 | 26.64 | 0.25218
72 | 80-40-SS-DW-32 | Distillate | D25 | 0.070788 | 994.1208 | 0.02 | 67.3287 | 77.92 | 0.014933
STEAM LINE
73 | XXX-40-SS-ST-01 | Steam | S1 | 1.5 | 0.16317 | 35 | 578.2911 | Plate
74 | XXX-40-SS-ST-02 | Steam | S2 | 1.3 | 0.13921 | 35 | 582.8509 | Plate
75 | ID720-THK-SS-ST-03 | Steam | S3 | 1.16 | 0.12016 | 24 | 715.6464 | Plate
76 | XXX-40-SS-ST-04 | Steam | S4 | 1.08 | 0.10435 | 35 | 613.6019 | Plate
77 | XXX-40-SS-ST-05 | Steam | S5 | 1.06 | 0.09086 | 35 | 651.4598 | Plate
78 | ID820-THK-SS-ST-06 | Steam | S6 | 1.08 | 0.07892 | 26 | 818.6282 | Plate
79 | XXX-40-SS-ST-07 | Steam | S7 | 1.15 | 0.06791 | 35 | 784.8797 | Plate
80 | XXX-40-SS-ST-08 | Steam | S8 | 1.3 | 0.05745 | 35 | 907.2933 | Plate
81 | ID1100-THK-SS-ST-09 | Steam | S9 | 1.84 | 0.04722 | 41 | 1100.0415 | Plate
82 | XXX-40-SS-ST-10 | Steam | S10 | 0 | 0 | 35 |  | Check Size
83 | XXX-40-SS-ST-11 | Steam | S11 | 0 | 0 | 35 |  | Check Size
84 | XXX-40-SS-ST-12 | Steam | S12 | 0 | 0 | 35 |  | Check Size
85 | 500-40-SS-ST-13 | Steam | S13 | 0.29 | 0.047309 | 36 | 465.617 | 477.82 | 34.1847
86 | 150-40-SS-ST-14 | Steam | S14 | 0.041165 | 0.20256 | 25 | 101.7358 | 154.08 | 10.8992
NCG LINE
87 | 40-40-SS-NCG-01 | Non-Condensable Gas | NCG1 | 0.00012614 | 0.3286 | 0.5 | 31.265 | 40.94 | 0.2916
88 | 40-40-SS-NCG-02 | Non-Condensable Gas | NCG2 | 0.00025681 | 0.25988 | 1 | 35.4711 | 40.94 | 0.75068
89 | 40-40-SS-NCG-03 | Non-Condensable Gas | NCG3 | 0.00039786 | 0.21216 | 1.5 | 39.897 | 40.94 | 1.4245
90 | 50-40-SS-NCG-04 | Non-Condensable Gas | NCG4 | 0.00055731 | 0.18041 | 2 | 44.3467 | 52.48 | 1.4281
91 | 50-40-SS-NCG-05 | Non-Condensable Gas | NCG5 | 0.00073814 | 0.15148 | 3 | 45.4763 | 52.48 | 2.2527
92 | 50-40-SS-NCG-06 | Non-Condensable Gas | NCG6 | 0.00095906 | 0.12632 | 4 | 49.1594 | 52.48 | 3.5098
93 | 50-40-SS-NCG-07 | Non-Condensable Gas | NCG7 | 0.001181 | 0.10741 | 6 | 48.3041 | 52.48 | 5.0831
94 | 100-40-SS-NCG-08 | Non-Condensable Gas | NCG8 | 0.0057625 | 0.072102 | 12 | 92.0866 | 102.26 | 9.7311
95 | 200-40-SS-NCG-09 | Non-Condensable Gas | NCG9 | 0.032908 | 0.056642 | 20 | 192.3204 | 202.74 | 17.9971
96 | XX-40-SS-NCG-10 | Non-Condensable Gas | NCG10 | 0 | 0 | 45 |  | Check Size
97 | XX-40-SS-NCG-11 | Non-Condensable Gas | NCG11 | 0 | 0 | 45 |  | Check Size
DOSING LINE
98 | XX-40-SS-DO-01 |  |  | HOLD
99 | XX-40-SS-DO-02 |  |  | HOLD
100 | XX-40-SS-DO-03 |  |  | HOLD
SERVICE LINE
101 | 50-40-SS-SE-01 |  |  | HOLD
102 | 50-40-SS-SE-02 |  |  | HOLD
103 | 50-40-SS-SE-03 |  |  | HOLD
104 | 50-40-SS-SE-04 |  |  | HOLD
VENT LINE
105 | 15-40-SS-VE-01 |  |  | HOLD
106 | 15-40-SS-VE-02 |  |  | HOLD
107 | 15-40-SS-VE-03 |  |  | HOLD
108 | 15-40-SS-VE-04 |  |  | HOLD
FEED WATER LINE
109 | 80-40-SS-FE-01 | Feed Water | F1 | 5.5698 | 1029.6111 | 1.5 | 67.7632 | 77.92 | 1.1344
110 | 25-40-SS-FE-1.1 | Feed Water | F1.1 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
111 | 25-40-SS-FE-1.2 | Feed Water | F1.2 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
112 | 25-40-SS-FE-1.3 | Feed Water | F1.3 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
113 | 25-40-SS-FE-1.4 | Feed Water | F1.4 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
114 | 25-40-SS-FE-1.5 | Feed Water | F1.5 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
115 | 25-40-SS-FE-1.6 | Feed Water | F1.6 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
116 | 25-40-SS-FE-1.7 | Feed Water | F1.7 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
117 | 25-40-SS-FE-1.8 | Feed Water | F1.8 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
118 | 25-40-SS-FE-1.9 | Feed Water | F1.9 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
119 | 25-40-SS-FE-1.10 | Feed Water | F1.10 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
120 | 80-40-SS-FE-02 | Feed Water | F2 | 5.5698 | 1029.6111 | 1.5 | 67.7632 | 77.92 | 1.1344
121 | 25-40-SS-FE-2.1 | Feed Water | F2.1 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
122 | 25-40-SS-FE-2.2 | Feed Water | F2.2 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
123 | 25-40-SS-FE-2.3 | Feed Water | F2.3 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
124 | 25-40-SS-FE-2.4 | Feed Water | F2.4 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
125 | 25-40-SS-FE-2.5 | Feed Water | F2.5 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
126 | 25-40-SS-FE-2.6 | Feed Water | F2.6 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
127 | 25-40-SS-FE-2.7 | Feed Water | F2.7 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
128 | 25-40-SS-FE-2.8 | Feed Water | F2.8 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
129 | 25-40-SS-FE-2.9 | Feed Water | F2.9 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
130 | 25-40-SS-FE-2.10 | Feed Water | F2.10 | 0.55698 | 1029.6111 | 2 | 18.5577 | 26.64 | 0.97053
131 | 80-40-SS-FE-03 | Feed Water | F3 | 5.5598 | 1029.6111 | 1.5 | 67.7024 | 77.92 | 1.1324
132 | 25-40-SS-FE-3.1 | Feed Water | F3.1 | 0.55598 | 1029.6111 | 2 | 18.5411 | 26.64 | 0.96879
133 | 25-40-SS-FE-3.2 | Feed Water | F3.2 | 0.55598 | 1029.6111 | 2 | 18.5411 | 26.64 | 0.96879
134 | 25-40-SS-FE-3.3 | Feed Water | F3.3 | 0.55598 | 1029.6111 | 2 | 18.5411 | 26.64 | 0.96879
135 | 25-40-SS-FE-3.4 | Feed Water | F3.4 | 0.55598 | 1029.6111 | 2 | 18.5411 | 26.64 | 0.96879
136 | 25-40-SS-FE-3.5 | Feed Water | F3.5 | 0.55598 | 1029.6111 | 2 | 18.5411 | 26.64 | 0.96879
137 | 25-40-SS-FE-3.6 | Feed Water | F3.6 | 0.55598 | 1029.6111 | 2 | 18.5411 | 26.64 | 0.96879
138 | 25-40-SS-FE-3.7 | Feed Water | F3.7 | 0.55598 | 1029.6111 | 2 | 18.5411 | 26.64 | 0.96879
139 | 25-40-SS-FE-3.8 | Feed Water | F3.8 | 0.55598 | 1029.6111 | 2 | 18.5411 | 26.64 | 0.96879
140 | 25-40-SS-FE-3.9 | Feed Water | F3.9 | 0.55598 | 1029.6111 | 2 | 18.5411 | 26.64 | 0.96879
141 | 25-40-SS-FE-3.10 | Feed Water | F3.10 | 0.55598 | 1029.6111 | 2 | 18.5411 | 26.64 | 0.96879
142 | 80-40-SS-FE-04 | Feed Water | F4 | 5.61 | 1030.8208 | 1.5 | 67.9672 | 77.92 | 1.1413
143 | 25-40-SS-FE-4.1 | Feed Water | F4.1 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
144 | 25-40-SS-FE-4.2 | Feed Water | F4.2 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
145 | 25-40-SS-FE-4.3 | Feed Water | F4.3 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
146 | 25-40-SS-FE-4.4 | Feed Water | F4.4 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
147 | 25-40-SS-FE-4.5 | Feed Water | F4.5 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
148 | 25-40-SS-FE-4.6 | Feed Water | F4.6 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
149 | 25-40-SS-FE-4.7 | Feed Water | F4.7 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
150 | 25-40-SS-FE-4.8 | Feed Water | F4.8 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
151 | 25-40-SS-FE-4.9 | Feed Water | F4.9 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
152 | 25-40-SS-FE-4.10 | Feed Water | F4.10 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
153 | 80-40-SS-FE-05 | Feed Water | F5 | 5.61 | 1030.8208 | 1.5 | 67.9672 | 77.92 | 1.1413
154 | 25-40-SS-FE-5.1 | Feed Water | F5.1 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
155 | 25-40-SS-FE-5.2 | Feed Water | F5.2 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
156 | 25-40-SS-FE-5.3 | Feed Water | F5.3 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
157 | 25-40-SS-FE-5.4 | Feed Water | F5.4 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
158 | 25-40-SS-FE-5.5 | Feed Water | F5.5 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
159 | 25-40-SS-FE-5.6 | Feed Water | F5.6 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
160 | 25-40-SS-FE-5.7 | Feed Water | F5.7 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
161 | 25-40-SS-FE-5.8 | Feed Water | F5.8 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
162 | 25-40-SS-FE-5.9 | Feed Water | F5.9 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
163 | 25-40-SS-FE-5.10 | Feed Water | F5.10 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
164 | 80-40-SS-FE-06 | Feed Water | F6 | 5.61 | 1030.8208 | 1.5 | 67.9672 | 77.92 | 1.1413
165 | 25-40-SS-FE-6.1 | Feed Water | F6.1 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
166 | 25-40-SS-FE-6.2 | Feed Water | F6.2 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
167 | 25-40-SS-FE-6.3 | Feed Water | F6.3 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
168 | 25-40-SS-FE-6.4 | Feed Water | F6.4 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
169 | 25-40-SS-FE-6.5 | Feed Water | F6.5 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
170 | 25-40-SS-FE-6.6 | Feed Water | F6.6 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
171 | 25-40-SS-FE-6.7 | Feed Water | F6.7 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
172 | 25-40-SS-FE-6.8 | Feed Water | F6.8 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
173 | 25-40-SS-FE-6.9 | Feed Water | F6.9 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
174 | 25-40-SS-FE-6.10 | Feed Water | F6.10 | 0.561 | 1030.8208 | 2 | 18.6136 | 26.64 | 0.97639
175 | 80-40-SS-FE-07 | Feed Water | F7 | 5.8267 | 1030.7582 | 1.5 | 69.2694 | 77.92 | 1.1854
176 | 25-40-SS-FE-7.1 | Feed Water | F7.1 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
177 | 25-40-SS-FE-7.2 | Feed Water | F7.2 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
178 | 25-40-SS-FE-7.3 | Feed Water | F7.3 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
179 | 25-40-SS-FE-7.4 | Feed Water | F7.4 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
180 | 25-40-SS-FE-7.5 | Feed Water | F7.5 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
181 | 25-40-SS-FE-7.6 | Feed Water | F7.6 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
182 | 25-40-SS-FE-7.7 | Feed Water | F7.7 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
183 | 25-40-SS-FE-7.8 | Feed Water | F7.8 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
184 | 25-40-SS-FE-7.9 | Feed Water | F7.9 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
185 | 25-40-SS-FE-7.10 | Feed Water | F7.10 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
186 | 80-40-SS-FE-08 | Feed Water | F8 | 5.8267 | 1030.7582 | 1.5 | 69.2694 | 77.92 | 1.1854
187 | 25-40-SS-FE-8.1 | Feed Water | F8.1 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
188 | 25-40-SS-FE-8.2 | Feed Water | F8.2 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
189 | 25-40-SS-FE-8.3 | Feed Water | F8.3 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
190 | 25-40-SS-FE-8.4 | Feed Water | F8.4 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
191 | 25-40-SS-FE-8.5 | Feed Water | F8.5 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
192 | 25-40-SS-FE-8.6 | Feed Water | F8.6 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
193 | 25-40-SS-FE-8.7 | Feed Water | F8.7 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
194 | 25-40-SS-FE-8.8 | Feed Water | F8.8 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
195 | 25-40-SS-FE-8.9 | Feed Water | F8.9 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
196 | 25-40-SS-FE-8.10 | Feed Water | F8.10 | 0.58267 | 1030.7582 | 2 | 18.9702 | 26.64 | 1.0142
197 | 80-40-SS-FE-09 | Feed Water | F9 | 5.8267 | 1030.7582 | 1.5 | 69.2694 | 77.92 | 1.1854
198 | 25-40-SS-FE-9.1 | Feed Water | F9.1 | 0.97111 | 1030.7582 | 3 | 19.9963 | 26.64 | 1.6903
199 | 25-40-SS-FE-9.2 | Feed Water | F9.2 | 0.97111 | 1030.7582 | 3 | 19.9963 | 26.64 | 1.6903
200 | 25-40-SS-FE-9.3 | Feed Water | F9.3 | 0.97111 | 1030.7582 | 3 | 19.9963 | 26.64 | 1.6903
201 | 25-40-SS-FE-9.4 | Feed Water | F9.4 | 0.97111 | 1030.7582 | 3 | 19.9963 | 26.64 | 1.6903
202 | 25-40-SS-FE-9.5 | Feed Water | F9.5 | 0.97111 | 1030.7582 | 3 | 19.9963 | 26.64 | 1.6903
203 | 25-40-SS-FE-9.6 | Feed Water | F9.6 | 0.97111 | 1030.7582 | 3 | 19.9963 | 26.64 | 1.6903

## LIST OF INSTRUMENTS
S.No | P&ID No | Line No. | TAG NO. | INSTRUMENT VALVE No. | SERVICE LOCATION | INSTRUMENT TYPE | Fluid | Operation Condition | [11 empty] | Instrument data | [5 empty] | Reference Hookup Diagram | Signal Type & Location |  |  | Instrument Model No | Accessories (Monifold/ TE/TW, etc,) | Remarks
[8 empty] | Pressure (m bar (a)) |  |  | Temperature (Deg C) |  |  | Flow rate (kg/hr) |  |  | TDS (ppm) |  |  | Inst. Range | Type | End connection | MOC | Installation | Accessories |  | Local | PLC | I/O Type
[8 empty] | Min. | Nor. | Max. | Min. | Nor. | Max. | Min. | Nor. | Max. | Min. | Nor. | Max.
1 | SP40-01-03-001 | 200-40-SS-SW-01 | PIT-101 | IV-101 | Suction Side - Sea water pump skid | Pressure Indicating Transmitter | Sea water |  | 1000 |  |  | 30 |  |  | 115522.2143 |  |  | 39504.4316
2 | SP40-01-03-001 | 200-40-SS-SW-02 | PG-101 | IV-102 | Sea water pump-1 discharge pressure | Pressure Gauge | Sea water |  | 3500 |  |  | 30.0862 |  |  | 115522.2143 |  |  | 39504.4316
3 | SP40-01-03-001 | 200-40-SS-SW-02 | PG-102 | IV-103 | Discharge Side - Sea water pump-2 | Pressure Gauge | Sea water |  | 3500 |  |  | 30.0862 |  |  | 115522.2143 |  |  | 39504.4316
4 | SP40-01-03-001 | 200-40-SS-SW-02 | PSL-101 | IV-104 | Discharge Side - Sea water pump | Pressure Switch | Sea water |  | 3500 |  |  | 30.0862 |  |  | 115522.2143 |  |  | 39504.4316
5 | SP40-01-03-001 | 200-40-SS-SW-02 | PIT-102 | IV-105 | Discharge Side - Sea water pump skid | Pressure Indicating Transmitter | Sea water |  | 3500 |  |  | 30.0862 |  |  | 115522.2143 |  |  | 39504.4316
6 | SP40-01-03-001 | 200-40-SS-SW-02 | TE-101 |  | Delivery Side - Sea water pump | Temperature Element with TW | Sea water |  | 3500 |  |  | 30.0862 |  |  | 115522.2143 |  |  | 39504.4316
7 | SP40-01-03-001 | 200-40-SS-SW-02 | TIT-101 |  | Delivery Side - Sea water pump skid | Temperature Indicating Transmitter | Sea water |  | 3500 |  |  | 30.0862 |  |  | 115522.2143 |  |  | 39504.4316
8 | SP40-01-03-001 | 200-40-SS-SW-02 | FIT-110 |  | Delivery Side - Sea water pump skid | Electro Magnetic Flow meter | Sea water |  | 3500 |  |  | 30.0862 |  |  | 115522.2143 |  |  | 39504.4316
9 | SP40-01-03-001 | 200-40-SS-SW-02 | CIT-101 | IV-109 | Delivery Side - Sea water pump skid | Conductivity Transmitter | Sea water |  | 3500 |  |  | 30.0862 |  |  | 115522.2143 |  |  | 39504.4316
10 | SP40-01-03-001 | 100-40-SS-SW-04 | PIT-103 | IV-106 | Distillate Plate Heat Exchanger - Outlet | Pressure Indicating Transmitter | Sea water |  | 3500 |  |  | 36 |  |  | 40282.2143 |  |  | 39504.4316
11 | SP40-01-03-001 | 100-40-SS-SW-04 | TE-102 |  | Distillate Plate Heat Exchanger - Outlet | Temperature Element with TW | Sea water |  | 3500 |  |  | 36 |  |  | 40282.2143 |  |  | 39504.4316
12 | SP40-01-03-001 | 100-40-SS-SW-04 | TIT-102 |  | Distillate Plate Heat Exchanger - Outlet | Temperature Indicating Transmitter | Sea water |  | 3500 |  |  | 36 |  |  | 40282.2143 |  |  | 39504.4316
13 | SP40-01-03-002 | 65-40-SS-SW-05 | ZT-101 |  | MED - 1st effect | Position Transmitter | Sea water |  | 3500 |  |  | 36 |  |  | 13427.4048 |  |  | 39504.4316
14 | SP40-01-03-002 | 65-40-SS-SW-05 | FIT-101 |  | MED - 1st effect sea water flow | Electro Magnetic Flow meter | Sea water |  | 3500 |  |  | 36 |  |  | 13427.4048 |  |  | 39504.4316
15 | SP40-01-03-002 | 65-40-SS-SW-06 | ZT-102 |  | MED - 2nd effect | Position Transmitter | Sea water |  | 3500 |  |  | 36 |  |  | 13427.4048 |  |  | 39504.4316
16 | SP40-01-03-002 | 65-40-SS-SW-06 | FIT-102 |  | MED - 2nd effect sea water flow | Electro Magnetic Flow meter | Sea water |  | 3500 |  |  | 36 |  |  | 13427.4048 |  |  | 39504.4316
17 | SP40-01-03-002 | 65-40-SS-SW-07 | ZT-103 |  | MED - 3rd effect | Position Transmitter | Sea water |  | 3500 |  |  | 36 |  |  | 13427.4048 |  |  | 39504.4316
18 | SP40-01-03-002 | 65-40-SS-SW-07 | FIT-103 |  | MED - 3rd effect sea water flow | Electro Magnetic Flow meter | Sea water |  | 3500 |  |  | 36 |  |  | 13427.4048 |  |  | 39504.4316
19 | SP40-01-03-001 | 100-40-SS-SW-09 | PIT-104 | IV-107 | Brine Plate Heat Exchanger - Outlet | Pressure Indicating Transmitter | Sea water |  | 3500 |  |  | 36.45 |  |  | 35640 |  |  | 39504.4316
20 | SP40-01-03-001 | 100-40-SS-SW-09 | TE-103 |  | Brine Plate Heat Exchanger - Outlet | Temperature Element with TW | Sea water |  | 3500 |  |  | 36.45 |  |  | 35640 |  |  | 39504.4316
21 | SP40-01-03-001 | 100-40-SS-SW-09 | TIT-103 |  | Brine Plate Heat Exchanger - Outlet | Temperature Indicating Transmitter | Sea water |  | 3500 |  |  | 36.45 |  |  | 35640 |  |  | 39504.4316
22 | SP40-01-03-002 | 65-40-SS-SW-10 | ZT-104 |  | MED - 4th effect | Position Transmitter | Sea water |  | 3500 |  |  | 36.45 |  |  | 11880 |  |  | 39504.4316
23 | SP40-01-03-002 | 65-40-SS-SW-10 | FIT-104 |  | MED - 4th effect sea water flow | Electro Magnetic Flow meter | Sea water |  | 3500 |  |  | 36.45 |  |  | 11880 |  |  | 39504.4316
24 | SP40-01-03-002 | 65-40-SS-SW-11 | ZT-105 |  | MED - 5th effect | Position Transmitter | Sea water |  | 3500 |  |  | 36.45 |  |  | 11880 |  |  | 39504.4316
25 | SP40-01-03-002 | 65-40-SS-SW-11 | FIT-105 |  | MED - 5th effect sea water flow | Electro Magnetic Flow meter | Sea water |  | 3500 |  |  | 36.45 |  |  | 11880 |  |  | 39504.4316
26 | SP40-01-03-002 | 65-40-SS-SW-12 | ZT-106 |  | MED - 6th effect | Position Transmitter | Sea water |  | 3500 |  |  | 36.45 |  |  | 11880 |  |  | 39504.4316
27 | SP40-01-03-002 | 65-40-SS-SW-12 | FIT-106 |  | MED - 6th effect sea water flow | Electro Magnetic Flow meter | Sea water |  | 3500 |  |  | 36.45 |  |  | 11880 |  |  | 39504.4316
28 | SP40-01-03-001 | 100-40-SS-SW-14 | PIT-105 | IV-108 | Final Condenser - Outlet | Pressure Indicating Transmitter | Sea water |  | 3500 |  |  | 33.9094 |  |  | 39600 |  |  | 39504.4316
29 | SP40-01-03-001 | 100-40-SS-SW-14 | TE-104 |  | Final Condenser - Outlet | Temperature Element with TW | Sea water |  | 3500 |  |  | 33.9094 |  |  | 39600 |  |  | 39504.4316
30 | SP40-01-03-001 | 100-40-SS-SW-14 | TIT-104 |  | Final Condenser - Outlet | Temperature Indicating Transmitter | Sea water |  | 3500 |  |  | 33.9094 |  |  | 39600 |  |  | 39504.4316
31 | SP40-01-03-002 | 65-40-SS-SW-15 | ZT-107 |  | MED - 7th effect | Position Transmitter | Sea water |  | 3500 |  |  | 33.9094 |  |  | 13200 |  |  | 39504.4316
32 | SP40-01-03-002 | 65-40-SS-SW-15 | FIT-107 |  | MED - 7th effect sea water flow | Electro Magnetic Flow meter | Sea water |  | 3500 |  |  | 33.9094 |  |  | 13200 |  |  | 39504.4316
33 | SP40-01-03-002 | 65-40-SS-SW-16 | ZT-108 |  | MED - 8th effect | Position Transmitter | Sea water |  | 3500 |  |  | 33.9094 |  |  | 13200 |  |  | 39504.4316
34 | SP40-01-03-002 | 65-40-SS-SW-16 | FIT-108 |  | MED - 8th effect sea water flow | Electro Magnetic Flow meter | Sea water |  | 3500 |  |  | 33.9094 |  |  | 13200 |  |  | 39504.4316
35 | SP40-01-03-002 | 65-40-SS-SW-17 | ZT-109 |  | MED - 9th effect | Position Transmitter | Sea water |  | 3500 |  |  | 33.9094 |  |  | 13200 |  |  | 39504.4316
36 | SP40-01-03-002 | 65-40-SS-SW-17 | FIT-109 |  | MED - 9th effect sea water flow | Electro Magnetic Flow meter | Sea water |  | 3500 |  |  | 33.9094 |  |  | 13200 |  |  | 39504.4316
37 | SP40-01-03-002 | MED - E1 | LG-201 |  | MED - 1st effect brine level | Level Gauge | Brine |  | 320.46 |  |  | 70.6
38 | SP40-01-03-002 | MED - E1 | LT-201 | IV-211 & IV-212 | MED - 1st effect brine level | Level Transmitter | Brine |  | 320.46 |  |  | 70.6
39 | SP40-01-03-002 | MED - E1 | LSH-201 |  | MED - 1st effect brine water LSH | Level Switch High | Brine |  | 320.46 |  |  | 70.6
40 | SP40-01-03-002 | MED - E1 | LSL-201 |  | MED - 1st effect brine water LSL | Level Switch Low | Brine |  | 320.46 |  |  | 70.6
41 | SP40-01-03-002 | 150-40-SS-BW-01 | TE-210 |  | 1st effect to 2nd effect siphon | Temperature Element with TW | Brine |  | 259.4 |  |  | 66.55 |  |  | 14652 |  |  | 63600
42 | SP40-01-03-002 | 150-40-SS-BW-01 | TIT-210 |  | 1st effect to 2nd effect siphon | Temperature Indicating Transmitter | Brine |  | 259.4 |  |  | 66.55 |  |  | 14652 |  |  | 63600
43 | SP40-01-03-001 | Brine Tank | LG-202 |  | Brine Tank - Brine level | Level Gauge | Brine |  | 68 |  |  | 39
44 | SP40-01-03-001 | Brine Tank | LT-202 | IV-213 & IV-214 | Brine Tank - Brine level | Level Transmitter | Brine |  | 68 |  |  | 39
45 | SP40-01-03-001 | Brine Tank | LSH-202 |  | Brine Tank - Brine water LSH | Level Switch High | Brine |  | 68 |  |  | 39
46 | SP40-01-03-001 | Brine Tank | LSL-202 |  | Brine Tank - Brine water LSL | Level Switch Low | Brine |  | 68 |  |  | 39
47 | SP40-01-03-001 | XX-XX-SS-BW-11 | PG-201 | IV-215 | Brine Re-Circulation pump 1 - Discharge pressure | Pressure Gauge | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
48 | SP40-01-03-001 | XX-XX-SS-BW-11 | PG-202 | IV-216 | Brine Re-Circulation pump 2 - Discharge pressure | Pressure Gauge | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
49 | SP40-01-03-001 | XX-XX-SS-BW-11 | PSL-201 | IV-217 | Brine Plate Heat Exchanger - Inlet | Pressure Switch | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
50 | SP40-01-03-001 | XX-XX-SS-BW-11 | PIT-211 | IV-218 | Brine Plate Heat Exchanger - Inlet | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
51 | SP40-01-03-001 | XX-XX-SS-BW-11 | TE-211 |  | Brine Plate Heat Exchanger - Inlet | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
52 | SP40-01-03-001 | XX-XX-SS-BW-11 | TIT-211 |  | Brine Plate Heat Exchanger - Inlet | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
53 | SP40-01-03-001 | 200-40-SS-BW-12 | PIT-202 | IV-219 | Brine Plate Heat Exchanger - Outlet | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
54 | SP40-01-03-001 | 200-40-SS-BW-12 | CIT-201 | IV-220 | Brine Plate Heat Exchanger - Outlet | Conductivity Transmitter | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
55 | SP40-01-03-001 | 200-40-SS-BW-12 | TE-212 |  | Brine Plate Heat Exchanger - Outlet | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
56 | SP40-01-03-001 | 200-40-SS-BW-12 | TIT-212 |  | Brine Plate Heat Exchanger - Outlet | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
57 | SP40-01-03-001 | 200-40-SS-BW-12 | ZT-210 |  | Brine Plate Heat Exchanger - Outlet | Position Transmitter | Brine |  | 2500 |  |  | 37.4474 | [5 empty] | 0
58 | SP40-01-03-002 | 150-40-SS-BW-13 | PIT-210 | IV-210 | Brine make-up line header | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 68130 |  |  | 60600
59 | SP40-01-03-002 | 80-40-SS-BW-15 | ZT-201 |  | MED - 1st effect | Position Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6624 |  |  | 60600
60 | SP40-01-03-002 | 80-40-SS-BW-15 | FIT-201 |  | MED - 1st effect | Electro Magnetic Flow meter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6624 |  |  | 60600
61 | SP40-01-03-002 | 80-40-SS-BW-15 | PIT-201 | IV-201 | MED - 1st effect | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6624 |  |  | 60600
62 | SP40-01-03-002 | 80-40-SS-BW-15 | TE-201 |  | MED - 1st effect | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 |  |  | 6624 |  |  | 60600
63 | SP40-01-03-002 | 80-40-SS-BW-15 | TIT-201 |  | MED - 1st effect | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6624 |  |  | 60600
64 | SP40-01-03-002 | 80-40-SS-BW-16 | ZT-202 |  | MED - 2nd effect | Position Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6624 |  |  | 60600
65 | SP40-01-03-002 | 80-40-SS-BW-16 | FIT-202 |  | MED - 2nd effect | Electro Magnetic Flow meter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6624 |  |  | 60600
66 | SP40-01-03-002 | 80-40-SS-BW-16 | PIT-202 | IV-202 | MED - 2nd effect | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6624 |  |  | 60600
67 | SP40-01-03-002 | 80-40-SS-BW-16 | TE-202 |  | MED - 2nd effect | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 |  |  | 6624 |  |  | 60600
68 | SP40-01-03-002 | 80-40-SS-BW-16 | TIT-202 |  | MED - 2nd effect | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6624 |  |  | 60600
69 | SP40-01-03-002 | 80-40-SS-BW-17 | ZT-203 |  | MED - 3rd effect | Position Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6588 |  |  | 60600
70 | SP40-01-03-002 | 80-40-SS-BW-17 | FIT-203 |  | MED - 3rd effect | Electro Magnetic Flow meter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6588 |  |  | 60600
71 | SP40-01-03-002 | 80-40-SS-BW-17 | PIT-203 | IV-203 | MED - 3rd effect | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6588 |  |  | 60600
72 | SP40-01-03-002 | 80-40-SS-BW-17 | TE-203 |  | MED - 3rd effect | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 |  |  | 6588 |  |  | 60600
73 | SP40-01-03-002 | 80-40-SS-BW-17 | TIT-203 |  | MED - 3rd effect | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 6588 |  |  | 60600
74 | SP40-01-03-002 | 80-40-SS-BW-18 | ZT-204 |  | MED - 4th effect | Position Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
75 | SP40-01-03-002 | 80-40-SS-BW-18 | FIT-204 |  | MED - 4th effect | Electro Magnetic Flow meter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
76 | SP40-01-03-002 | 80-40-SS-BW-18 | PIT-204 | IV-204 | MED - 4th effect | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
77 | SP40-01-03-002 | 80-40-SS-BW-18 | TE-204 |  | MED - 4th effect | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
78 | SP40-01-03-002 | 80-40-SS-BW-18 | TIT-204 |  | MED - 4th effect | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
79 | SP40-01-03-002 | 80-40-SS-BW-19 | ZT-205 |  | MED - 5th effect | Position Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
80 | SP40-01-03-002 | 80-40-SS-BW-19 | FIT-205 |  | MED - 5th effect | Electro Magnetic Flow meter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
81 | SP40-01-03-002 | 80-40-SS-BW-19 | PIT-205 | IV-205 | MED - 5th effect | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
82 | SP40-01-03-002 | 80-40-SS-BW-19 | TE-205 |  | MED - 5th effect | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
83 | SP40-01-03-002 | 80-40-SS-BW-19 | TIT-205 |  | MED - 5th effect | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
84 | SP40-01-03-002 | 80-40-SS-BW-20 | ZT-206 |  | MED - 6th effect | Position Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
85 | SP40-01-03-002 | 80-40-SS-BW-20 | FIT-206 |  | MED - 6th effect | Electro Magnetic Flow meter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
86 | SP40-01-03-002 | 80-40-SS-BW-20 | PIT-206 | IV-206 | MED - 6th effect | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
87 | SP40-01-03-002 | 80-40-SS-BW-20 | TE-206 |  | MED - 6th effect | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
88 | SP40-01-03-002 | 80-40-SS-BW-20 | TIT-206 |  | MED - 6th effect | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 8316 |  |  | 60600
89 | SP40-01-03-002 | 80-40-SS-BW-21 | ZT-207 |  | MED - 7th effect | Position Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
90 | SP40-01-03-002 | 80-40-SS-BW-21 | FIT-207 |  | MED - 7th effect | Electro Magnetic Flow meter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
91 | SP40-01-03-002 | 80-40-SS-BW-21 | PIT-207 | IV-207 | MED - 7th effect | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
92 | SP40-01-03-002 | 80-40-SS-BW-21 | TE-207 |  | MED - 7th effect | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
93 | SP40-01-03-002 | 80-40-SS-BW-21 | TIT-207 |  | MED - 7th effect | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
94 | SP40-01-03-002 | 80-40-SS-BW-22 | ZT-208 |  | MED - 8th effect | Position Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
95 | SP40-01-03-002 | 80-40-SS-BW-22 | FIT-208 |  | MED - 8th effect | Electro Magnetic Flow meter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
96 | SP40-01-03-002 | 80-40-SS-BW-22 | PIT-208 | IV-208 | MED - 8th effect | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
97 | SP40-01-03-002 | 80-40-SS-BW-22 | TE-208 |  | MED - 8th effect | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
98 | SP40-01-03-002 | 80-40-SS-BW-22 | TIT-208 |  | MED - 8th effect | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
99 | SP40-01-03-002 | 80-40-SS-BW-23 | ZT-209 |  | MED - 9th effect | Position Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
100 | SP40-01-03-002 | 80-40-SS-BW-23 | FIT-209 |  | MED - 9th effect | Electro Magnetic Flow meter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
101 | SP40-01-03-002 | 80-40-SS-BW-23 | PIT-209 | IV-209 | MED - 9th effect | Pressure Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
102 | SP40-01-03-002 | 80-40-SS-BW-23 | TE-209 |  | MED - 9th effect | Temperature Element with TW | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
103 | SP40-01-03-002 | 80-40-SS-BW-23 | TIT-209 |  | MED - 9th effect | Temperature Indicating Transmitter | Brine |  | 2500 |  |  | 37.4474 |  |  | 7776 |  |  | 60600
104 | SP40-01-03-002 | MED - E1 | LG-301 |  | MED - 1st effect distillate level | Level Gauge | Distillate |  | 320.46 |  |  | 70.6
105 | SP40-01-03-002 | MED - E1 | LT-301 | IV-301 & IV-302 | MED - 1st effect distillate level | Level Transmitter | Distillate |  | 320.46 |  |  | 70.6
106 | SP40-01-03-002 | MED - E1 | LSH-301 |  | MED - 1st effect distillate water LSH | Level Switch High | Distillate |  | 320.46 |  |  | 70.6
107 | SP40-01-03-002 | MED - E1 | LSL-301 |  | MED - 1st effect distillate water LSL | Level Switch Low | Distillate |  | 320.46 |  |  | 70.6
108 | SP40-01-03-002 | Distillate Tank | LG-302 |  | Distillate Tank distillate level | Level Gauge | Distillate |  | 84.6 |  |  | 42.4045
109 | SP40-01-03-002 | Distillate Tank | LT-302 | IV-301 & IV-302 | Distillate Tank distillate level | Level Transmitter | Distillate |  | 84.6 |  |  | 42.4045
110 | SP40-01-03-002 | Distillate Tank | LSH-302 |  | Distillate Tank distillate water LSH | Level Switch High | Distillate |  | 84.6 |  |  | 42.4045
111 | SP40-01-03-002 | Distillate Tank | LSL-302 |  | Distillate Tank distillate water LSL | Level Switch Low | Distillate |  | 84.6 |  |  | 42.4045
112 | SP40-01-03-002 | 100-40-SS-DW-11 | PG-301 | IV-305 | DPHE - Suction | Pressure Gauge | Distillate |  | 0 |  |  | 42.4936 |  |  | 41688 |  |  | NIL
113 | SP40-01-03-002 | 100-40-SS-DW-11 | PG-302 | IV-306 | DPHE - Suction | Pressure Gauge | Distillate |  | 0 |  |  | 42.4936 |  |  | 41688 |  |  | NIL
114 | SP40-01-03-002 | 100-40-SS-DW-11 | PSL-301 | IV-307 | DPHE - Suction | Pressure Switch | Distillate |  | 0 |  |  | 42.4936 |  |  | 41688 |  |  | NIL
115 | SP40-01-03-002 | 100-40-SS-DW-11 | PIT-301 | IV-308 | DPHE - Suction | Pressure Indicating Transmitter | Distillate |  | 0 |  |  | 42.4936 |  |  | 41688 |  |  | NIL
116 | SP40-01-03-002 | 100-40-SS-DW-11 | TE-301 |  | DPHE - Suction | Temperature Element with TW | Distillate |  | 0 |  |  | 42.4936 |  |  | 41688 |  |  | NIL
117 | SP40-01-03-002 | 100-40-SS-DW-11 | TIT-301 |  | DPHE - Suction | Temperature Indicating Transmitter | Distillate |  | 0 |  |  | 42.4936 |  |  | 41688 |  |  | NIL
118 | SP40-01-03-002 | 100-40-SS-DW-12 | TE-302 |  | DPHE - Discharge | Temperature Element with TW | Distillate |  | 0 |  |  | 0 |  |  | 41688 |  |  | NIL
119 | SP40-01-03-002 | 100-40-SS-DW-12 | TIT-302 |  | DPHE - Discharge | Temperature Indicating Transmitter | Distillate |  | 0 |  |  | 0 |  |  | 41688 |  |  | NIL
120 | SP40-01-03-002 | 100-40-SS-DW-12 | CIT-301 | IV-309 | DPHE - Discharge | Conductivity Transmitter | Distillate |  | 0 |  |  | 0 |  |  | 41688 |  |  | NIL
121 | SP40-01-03-002 | 100-40-SS-DW-12 | FIT-301 |  | DPHE - Discharge | Electro Magnetic Flow meter | Distillate |  | 0 |  |  | 0 |  |  | 41688 |  |  | NIL
122 | SP40-01-03-003 | Distillate Storage Tank | LG-303 |  | LIT-303 | Level Gauge | Distillate |  | 0 |  |  | 0
123 | SP40-01-03-003 | Distillate Storage Tank | LT-303 | IV-310 & IV-311 | LIT-303 | Level Transmitter | Distillate |  | 0 |  |  | 0
124 | SP40-01-03-003 | Distillate Storage Tank | LSH-303 |  | LIT-303 | Level Switch High | Distillate |  | 0 |  |  | 0
125 | SP40-01-03-003 | Distillate Storage Tank | LSL-303 |  | LIT-303 | Level Switch Low | Distillate |  | 0 |  |  | 0
126 | SP40-01-03-003 | 100-40-SS-DW-16 | PG-303 | IV-312 | IFP - Discharge | Pressure Gauge | Distillate |  | 0 |  |  | 30 |  |  | 2199.6 |  |  | 0
127 | SP40-01-03-003 | 25-40-SS-DW-19 | PG-304 | IV-313 | MP-1 Discharge | Pressure Gauge | Distillate |  | 0 |  |  | 30 |  |  | 144 |  |  | 0
128 | SP40-01-03-003 | 25-40-SS-DW-19 | PG-305 | IV-314 | MP-2 Discharge | Pressure Gauge | Distillate |  | 0 |  |  | 30 |  |  | 144 |  |  | 0
129 | SP40-01-03-003 | 25-40-SS-DW-20 | PSL-302 | IV-315 | MP Skid discharge | Pressure Switch | Distillate |  | 0 |  |  | 30 |  |  | 144 |  |  | 0
130 | SP40-01-03-003 | 25-40-SS-DW-20 | PIT-302 | IV-316 | MP Skid discharge | Pressure indicating Transmitter | Distillate |  | 0 |  |  | 30 |  |  | 144 |  |  | 0
131 | SP40-01-03-003 | LTFV | LG-304 |  | LIT-303 | Level Gauge | Distillate |  | 67.9695 |  |  | 38.3888
132 | SP40-01-03-003 | LTFV | LT-304 | IV-317 & IV-318 | LIT-303 | Level Transmitter | Distillate |  | 67.9695 |  |  | 38.3888
133 | SP40-01-03-003 | LTFV | LSH-304 |  | LIT-303 | Level Switch High | Distillate |  | 67.9695 |  |  | 38.3888
134 | SP40-01-03-003 | LTFV | LSL-304 |  | LIT-303 | Level Switch Low | Distillate |  | 67.9695 |  |  | 38.3888
135 | SP40-01-03-003 | LTFV | TE-303 |  | LTFV | Temperature Element with TW | Distillate |  | 67.9695 |  |  | 38.3888
136 | SP40-01-03-003 | LTFV | TIT-303 |  | LTFV | Temperature Indicating Transmitter | Distillate |  | 67.9695 |  |  | 38.3888
137 | SP40-01-03-003 | 80-40-SS-DW-24 | PG-306 | IV-313 | LTFV-RCP-1 Discharge | Pressure Gauge | Distillate |  | 68 |  |  | 38.39 |  |  | 21456 |  |  | NIL
138 | SP40-01-03-003 | 80-40-SS-DW-24 | PG-307 | IV-314 | LTFV-RCP-2 Discharge | Pressure Gauge | Distillate |  | 68 |  |  | 38.39 |  |  | 21456 |  |  | NIL
139 | SP40-01-03-003 | 80-40-SS-DW-24 | PSL-303 | IV-315 | LTFV-RCP Skid discharge | Pressure Switch | Distillate |  | 68 |  |  | 38.39 |  |  | 21456 |  |  | NIL
140 | SP40-01-03-003 | 80-40-SS-DW-24 | PIT-303 | IV-316 | LTFV-RCP Skid discharge | Pressure indicating Transmitter | Distillate |  | 68 |  |  | 38.39 |  |  | 21456 |  |  | NIL
141 | SP40-01-03-003 | 80-40-SS-DW-25 | FIT-303 |  | LTFV - Distillate Inlet | Electro Magnetic Flow meter | Distillate |  | 1100 |  |  | 65 |  |  | 22500 |  |  | NIL
142 | SP40-01-03-003 | 80-40-SS-DW-25 | TE-304 |  | LTFV - Distillate Inlet | Temperature Element with TW | Distillate |  | 1100 |  |  | 65 |  |  | 22500 |  |  | NIL
143 | SP40-01-03-003 | 80-40-SS-DW-25 | TIT-304 |  | LTFV - Distillate Inlet | Temperature Indicating Transmitter | Distillate |  | 1100 |  |  | 65 |  |  | 22500 |  |  | NIL
144 | SP40-01-03-003 | 80-40-SS-DW-25 | LG-305 |  | LIT-305 | Level Gauge | Distillate |  | 1100 |  |  | 65 |  |  | 22500 |  |  | NIL
145 | SP40-01-03-003 | HTFV | LT-305 | IV-319 & IV-320 | LIT-305 | Level Transmitter | Distillate |  | 320.4559 |  |  | 70.6
146 | SP40-01-03-003 | HTFV | LSH-305 |  | LIT-305 | Level Switch High | Distillate |  | 320.4559 |  |  | 70.6
147 | SP40-01-03-003 | HTFV | LSL-305 |  | LIT-305 | Level Switch Low | Distillate |  | 320.4559 |  |  | 70.6
148 | SP40-01-03-003 | HTFV | TE-305 |  | HTFV | Temperature Element with TW | Distillate |  | 320.4559 |  |  | 70.6
149 | SP40-01-03-003 | HTFV | TIT-305 |  | HTFV | Temperature Indicating Transmitter | Distillate |  | 320.4559 |  |  | 70.6
150 | SP40-01-03-003 | 50-40-SS-DW-29 | PG-308 | IV-325 | HTFV-RCP-1 Discharge | Pressure Gauge | Distillate |  | 320.5 |  |  | 69.56 |  |  | 16411.8047 |  |  | NIL
151 | SP40-01-03-003 | 50-40-SS-DW-29 | PG-309 | IV-326 | HTFV-RCP-2 Discharge | Pressure Gauge | Distillate |  | 320.5 |  |  | 69.56 |  |  | 16411.8047 |  |  | NIL
152 | SP40-01-03-003 | 50-40-SS-DW-29 | PSL-304 | IV-327 | HTFV-RCP Skid discharge | Pressure Switch | Distillate |  | 320.5 |  |  | 69.56 |  |  | 16411.8047 |  |  | NIL
153 | SP40-01-03-003 | 50-40-SS-DW-29 | PIT-304 | IV-328 | HTFV-RCP Skid discharge | Pressure indicating Transmitter | Distillate |  | 320.5 |  |  | 69.56 |  |  | 16411.8047 |  |  | NIL
154 | SP40-01-03-003 | 50-40-SS-DW-30 | FIT-304 |  | HTFV - Distillate Inlet | Electro Magnetic Flow meter | Distillate |  | 1200 |  |  | 78 |  |  | 11160 |  |  | NIL
155 | SP40-01-03-003 | 50-40-SS-DW-30 | TE-306 |  | HTFV - Distillate Inlet | Temperature Element with TW | Distillate |  | 1200 |  |  | 78 |  |  | 11160 |  |  | NIL
156 | SP40-01-03-003 | 50-40-SS-DW-30 | TIT-306 |  | HTFV - Distillate Inlet | Temperature Indicating Transmitter | Distillate |  | 1200 |  |  | 78 |  |  | 11160 |  |  | NIL
157 | SP40-01-03-001 | 80-40-SS-DW-32 | TE-307 |  | Final Condenser - Distillate outlet | Temperature Element with TW | Distillate |  | 67.97 |  |  | 34.9098 |  |  | 254.837 |  |  | NIL
158 | SP40-01-03-001 | 80-40-SS-DW-32 | TIT-307 |  | Final Condenser - Distillate outlet | Temperature Indicating Transmitter | Distillate |  | 67.97 |  |  | 34.9098 |  |  | 254.837 |  |  | NIL
159 | SP40-01-03-002 | ID1100-THK-SS-ST-09 | PIT-402 | IV-402 | Effect 9 to MVC 1 suction side | Pressure Indicating Transmitter | Steam |  | 68 |  |  | 39 |  |  | 6624 |  |  | NIL
160 | SP40-01-03-002 | ID1100-THK-SS-ST-09 | TE-402 |  | Effect 9 to MVC 1 suction side | Temperature Element with TW | Steam |  | 68 |  |  | 39 |  |  | 6624 |  |  | NIL
161 | SP40-01-03-002 | ID1100-THK-SS-ST-09 | TIT-402 |  | Effect 9 to MVC 1 suction side | Temperature Indicating Transmitter | Steam |  | 68 |  |  | 39 |  |  | 6624 |  |  | NIL
162 | SP40-01-03-002 | XXX-40-SS-ST-10 | PIT-403 | IV-403 | MVC 1 delivery side | Pressure Indicating Transmitter | Steam |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
163 | SP40-01-03-002 | XXX-40-SS-ST-10 | TE-403 |  | MVC 1 delivery side | Temperature Element with TW | Steam |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
164 | SP40-01-03-002 | XXX-40-SS-ST-10 | TIT-403 |  | MVC 1 delivery side | Temperature Indicating Transmitter | Steam |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
165 | SP40-01-03-002 | XXX-40-SS-ST-11 | PIT-404 | IV-404 | MVC 2 delivery side | Pressure Indicating Transmitter | Steam |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
166 | SP40-01-03-002 | XXX-40-SS-ST-11 | TE-404 |  | MVC 2 delivery side | Temperature Element with TW | Steam |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
167 | SP40-01-03-002 | XXX-40-SS-ST-11 | TIT-404 |  | MVC 2 delivery side | Temperature Indicating Transmitter | Steam |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
168 | SP40-01-03-002 | XXX-40-SS-ST-12 | PIT-405 | IV-405 | MVC 3 delivery side | Pressure Indicating Transmitter | Steam |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
169 | SP40-01-03-002 | XXX-40-SS-ST-12 | TE-405 |  | MVC 3 delivery side | Temperature Element with TW | Steam |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
170 | SP40-01-03-002 | XXX-40-SS-ST-12 | TIT-405 |  | MVC 3 delivery side | Temperature Indicating Transmitter | Steam |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
171 | SP40-01-03-002 | MED - E1 | PIT-407 | IV-407 | MED 1st Effect Vapour Box | Pressure Indicating Transmitter | Steam |  | 320.46 |  |  | 70.6
172 | SP40-01-03-002 | MED - E1 | TE-407 |  | MED 1st Effect Vapour Box | Temperature Element with TW | Steam |  | 320.46 |  |  | 70.6
173 | SP40-01-03-002 | MED - E1 | TIT-407 |  | MED 1st Effect Vapour Box | Temperature Indicating Transmitter | Steam |  | 320.46 |  |  | 70.6
174 | SP40-01-03-002 | MED - E1 | PIT-408 | IV-408 | MED 1st Effect | Pressure Indicating Transmitter | Steam |  | 320.46 |  |  | 70.6
175 | SP40-01-03-002 | MED - E1 | TE-408 |  | MED 1st Effect | Temperature Element with TW | Steam |  | 320.46 |  |  | 70.6
176 | SP40-01-03-002 | MED - E1 | TIT-408 |  | MED 1st Effect | Temperature Indicating Transmitter | Steam |  | 320.46 |  |  | 70.6
177 | SP40-01-03-002 | MED - E2 | TG-401 |  | MED 2nd Effect Vapour Box | Temperature Gauge | Steam |  | 259.4 |  |  | 66.55
178 | SP40-01-03-002 | MED - E2 | PIT-409 | IV-409 | MED 2nd Effect | Pressure Indicating Transmitter | Steam |  | 259.4 |  |  | 66.55
179 | SP40-01-03-002 | MED - E2 | TE-409 |  | MED 2nd Effect | Temperature Element with TW | Steam |  | 259.4 |  |  | 66.55
180 | SP40-01-03-002 | MED - E2 | TIT-409 |  | MED 2nd Effect | Temperature Indicating Transmitter | Steam |  | 259.4 |  |  | 66.55
181 | SP40-01-03-002 | MED - E3 | TG-402 |  | MED 3rd Effect Vapour Box | Temperature Gauge | Steam |  | 219.6 |  |  | 62.81
182 | SP40-01-03-002 | MED - E3 | PIT-410 | IV-410 | MED 3rd Effect | Pressure Indicating Transmitter | Steam |  | 219.6 |  |  | 62.81
183 | SP40-01-03-002 | MED - E3 | TE-410 |  | MED 3rd Effect | Temperature Element with TW | Steam |  | 219.6 |  |  | 62.81
184 | SP40-01-03-002 | MED - E3 | TIT-410 |  | MED 3rd Effect | Temperature Indicating Transmitter | Steam |  | 219.6 |  |  | 62.81
185 | SP40-01-03-002 | MED - E4 | TG-403 |  | MED 4th Effect Vapour Box | Temperature Gauge | Steam |  | 188 |  |  | 59.4
186 | SP40-01-03-002 | MED - E4 | PIT-411 | IV-411 | MED 4th Effect | Pressure Indicating Transmitter | Steam |  | 188 |  |  | 59.4
187 | SP40-01-03-002 | MED - E4 | TE-411 |  | MED 4th Effect | Temperature Element with TW | Steam |  | 188 |  |  | 59.4
188 | SP40-01-03-002 | MED - E4 | TIT-411 |  | MED 4th Effect | Temperature Indicating Transmitter | Steam |  | 188 |  |  | 59.4
189 | SP40-01-03-002 | MED - E5 | TG-404 |  | MED 5th Effect Vapour Box | Temperature Gauge | Steam |  | 161.8 |  |  | 56.2
190 | SP40-01-03-002 | MED - E5 | PIT-412 | IV-412 | MED 5th Effect | Pressure Indicating Transmitter | Steam |  | 161.8 |  |  | 56.2
191 | SP40-01-03-002 | MED - E5 | TE-412 |  | MED 5th Effect | Temperature Element with TW | Steam |  | 161.8 |  |  | 56.2
192 | SP40-01-03-002 | MED - E5 | TIT-412 |  | MED 5th Effect | Temperature Indicating Transmitter | Steam |  | 161.8 |  |  | 56.2
193 | SP40-01-03-002 | MED - E6 | TG-405 |  | MED 6th Effect Vapour Box | Temperature Gauge | Steam |  | 139.5 |  |  | 53.1
194 | SP40-01-03-002 | MED - E6 | PIT-413 | IV-413 | MED 6th Effect | Pressure Indicating Transmitter | Steam |  | 139.5 |  |  | 53.1
195 | SP40-01-03-002 | MED - E6 | TE-413 |  | MED 6th Effect | Temperature Element with TW | Steam |  | 139.5 |  |  | 53.1
196 | SP40-01-03-002 | MED - E6 | TIT-413 |  | MED 6th Effect | Temperature Indicating Transmitter | Steam |  | 139.5 |  |  | 53.1
197 | SP40-01-03-002 | MED - E7 | TG-406 |  | MED 7th Effect Vapour Box | Temperature Gauge | Steam |  | 119.8 |  |  | 50
198 | SP40-01-03-002 | MED - E7 | PIT-414 | IV-414 | MED 7th Effect | Pressure Indicating Transmitter | Steam |  | 119.8 |  |  | 50
199 | SP40-01-03-002 | MED - E7 | TE-414 |  | MED 7th Effect | Temperature Element with TW | Steam |  | 119.8 |  |  | 50
200 | SP40-01-03-002 | MED - E7 | TIT-414 |  | MED 7th Effect | Temperature Indicating Transmitter | Steam |  | 119.8 |  |  | 50
201 | SP40-01-03-002 | MED - E8 | TG-407 |  | MED 8th Effect Vapour Box | Temperature Gauge | Steam |  | 101.7 |  |  | 46.72
202 | SP40-01-03-002 | MED - E8 | PIT-415 | IV-415 | MED 8th Effect | Pressure Indicating Transmitter | Steam |  | 101.7 |  |  | 46.72
203 | SP40-01-03-002 | MED - E8 | TE-415 |  | MED 8th Effect | Temperature Element with TW | Steam |  | 101.7 |  |  | 46.72
204 | SP40-01-03-002 | MED - E8 | TIT-415 |  | MED 8th Effect | Temperature Indicating Transmitter | Steam |  | 101.7 |  |  | 46.72
205 | SP40-01-03-002 | MED - E9 | TG-408 |  | MED 9th Effect Vapour Box | Temperature Gauge | Steam |  | 84.6 |  |  | 43.14
206 | SP40-01-03-002 | MED - E9 | PIT-416 | IV-416 | MED 9th Effect | Pressure Indicating Transmitter | Steam |  | 84.6 |  |  | 43.14
207 | SP40-01-03-002 | MED - E9 | TE-416 |  | MED 9th Effect | Temperature Element with TW | Steam |  | 84.6 |  |  | 43.14
208 | SP40-01-03-002 | MED - E9 | TIT-416 |  | MED 9th Effect | Temperature Indicating Transmitter | Steam |  | 84.6 |  |  | 43.14
209 | SP40-01-03-002 | MED - E9 | PIT-417 | IV-417 | MED 9th Effect | Pressure Indicating Transmitter | Steam |  | 84.6 |  |  | 43.14
210 | SP40-01-03-002 | MED - E9 | TE-417 |  | MED 9th Effect | Temperature Element with TW | Steam |  | 84.6 |  |  | 43.14
211 | SP40-01-03-002 | MED - E9 | TIT-417 |  | MED 9th Effect | Temperature Indicating Transmitter | Steam |  | 84.6 |  |  | 43.14
212 | SP40-01-03-003 | LTFV | PIT-401 | IV-401 | Low Temperature Flash Vessel | Pressure Indicating Transmitter | Steam |  | 67.9695 |  |  | 38.3888
213 | SP40-01-03-003 | LTFV | TE-401 |  | Low Temperature Flash Vessel | Temperature Element with TW | Steam |  | 67.9695 |  |  | 38.3888
214 | SP40-01-03-003 | LTFV | TIT-401 |  | Low Temperature Flash Vessel | Temperature Indicating Transmitter | Steam |  | 67.9695 |  |  | 38.3888
215 | SP40-01-03-003 | HTFV | PIT-406 | IV-406 | High Temperature Flash Vessel | Pressure Indicating Transmitter | Steam |  | 320.4559 |  |  | 70.6
216 | SP40-01-03-003 | HTFV | TE-406 |  | High Temperature Flash Vessel | Temperature Element with TW | Steam |  | 320.4559 |  |  | 70.6
217 | SP40-01-03-003 | HTFV | TIT-406 |  | High Temperature Flash Vessel | Temperature Indicating Transmitter | Steam |  | 320.4559 |  |  | 70.6
218 | SP40-01-03-001 | FC | PIT-501 | IV-501 | Final Condenser | Pressure Indicating Transmitter | NCG |  | 82 |  |  | 41.91
219 | SP40-01-03-001 | FC | TE-501 |  | Final Condenser | Temperature Element with TW | NCG |  | 82 |  |  | 41.91
220 | SP40-01-03-001 | FC | TIT-501 |  | Final Condenser | Temperature Indicating Transmitter | NCG |  | 82 |  |  | 41.91
221 | SP40-01-03-001 | 100-40-SS-NCG-10 | PG-501 | IV-502 | LRVP-1&2 Pump Suction Side | Pressure Gauge | NCG |  | #N/A |  |  | #N/A
222 | SP40-01-03-001 | 100-40-SS-NCG-11 | PG-502 | IV-503 | LRVP-1 Pump Discharge Side | Pressure Gauge | NCG |  | #N/A |  |  | #N/A
223 | SP40-01-03-001 | 100-40-SS-NCG-11 | PG-503 | IV-504 | LRVP-2 Pump Discharge Side | Pressure Gauge | NCG |  | #N/A |  |  | #N/A
224 | SP40-01-03-004 | Anti-Scalant Tank | LSL-601 |  | Anti-Scalant Tank | Limit Switch Low | Dosing |  | 0 |  |  | 0
225 | SP40-01-03-004 | Anti-Form Tank | LSL-602 |  | Anti-Form Tank | Limit Switch Low | Dosing |  | #N/A |  |  | #N/A
226 | SP40-01-03-004 | Acid Cleaning Tank | LSL-603 |  | Acid Cleaning Tank | Limit Switch Low | Dosing |  | 0 |  |  | 0

## LIST OF VALVES
S.No | P&ID No | LINE NUMBER | VALVE TAG No. | SERVICE LOACATION | VALVE TYPE | END CONNECTION | SIZE (NB) | Fluid | Operation Condition | [8 empty] | Delta Pressure (bar) | Instrument data | [7 empty] | Signal Type & Location |  |  | Instrument Model No | Accessories | Remarks
[9 empty] | Pressure (Bar) |  |  | Temperature (Deg C) |  |  | Flow (m3/hr) |  |  |  | Valve Operation | Type | End connection | Body | Trim | Seat | Packing material | Leakage Class | Local | PLC | I/O Type
[9 empty] | Min. | Nor. | Max. | Min. | Nor. | Max. | Min. | Nor. | Max.
1 | SP40-01-03-001 | 200-40-SS-SW-01 | IV-101 | PIT-101 - Isolation Valve | BALL VALVE | THREADED | NB15 | Sea water |  | 1 |  |  | 30 |  |  | 112.5594
2 | SP40-01-03-001 | 200-40-SS-SW-01 | BFV-101 | SWP-1 SUCTION SIDE | BUTTERFLY | FLANGED | NB200 | Sea water |  | 1 |  |  | 30 |  |  | 112.5594
3 | SP40-01-03-001 | 200-40-SS-SW-01 | BFV-102 | SWP-2 SUCTION SIDE | BUTTERFLY | FLANGED | NB200 | Sea water |  | 1 |  |  | 30 |  |  | 112.5594
4 | SP40-01-03-001 | 200-40-SS-SW-01 | DV-101 | ST-101 - Strainer drain valve | BALL VALVE | FLANGED | NB15 | Sea water |  | 1 |  |  | 30 |  |  | 112.5594
5 | SP40-01-03-001 | 200-40-SS-SW-01 | DV-102 | ST-102 - Strainer drain valve | BALL VALVE | FLANGED | NB15 | Sea water |  | 1 |  |  | 30 |  |  | 112.5594
6 | SP40-01-03-001 | 200-40-SS-SW-02 | IV-102 | PG-101 | BALL VALVE | THREADED | NB15 | Sea water |  | 3.5 |  |  | 30.0862 |  |  | 112.55
7 | SP40-01-03-001 | 200-40-SS-SW-02 | IV-103 | PG-102 | BALL VALVE | THREADED | NB15 | Sea water |  | 3.5 |  |  | 30.0862 |  |  | 112.55
8 | SP40-01-03-001 | 200-40-SS-SW-02 | NRV-101 | SWP-1 DELIVERY SIDE | NON RETURN VALVE | FLANGED | NB200 | Sea water |  | 3.5 |  |  | 30.0862 |  |  | 112.55
9 | SP40-01-03-001 | 200-40-SS-SW-02 | NRV-102 | SWP-2 DELIVERY SIDE | NON RETURN VALVE | FLANGED | NB200 | Sea water |  | 3.5 |  |  | 30.0862 |  |  | 112.55
10 | SP40-01-03-001 | 200-40-SS-SW-02 | BV-101 | SWP-1 DELIVERY SIDE | BALL VALVE | FLANGED | NB200 | Sea water |  | 3.5 |  |  | 30.0862 |  |  | 112.55
11 | SP40-01-03-001 | 200-40-SS-SW-02 | BV-102 | SWP-2 DELIVERY SIDE | BALL VALVE | FLANGED | NB200 | Sea water |  | 3.5 |  |  | 30.0862 |  |  | 112.55
12 | SP40-01-03-001 | 200-40-SS-SW-02 | IV-104 | PSL-101 | BALL VALVE | THREADED | NB15 | Sea water |  | 3.5 |  |  | 30.0862 |  |  | 112.55
13 | SP40-01-03-001 | 200-40-SS-SW-02 | IV-105 | PIT-102 | BALL VALVE | THREADED | NB15 | Sea water |  | 3.5 |  |  | 30.0862 |  |  | 112.55
14 | SP40-01-03-001 | 200-40-SS-SW-02 | IV-109 | CIT-101 | BALL VALVE | THREADED | NB15 | Sea water |  | 3.5 |  |  | 30.0862 |  |  | 112.55
15 | SP40-01-03-001 | 100-40-SS-SW-04 | IV-106 | PIT-103 | BALL VALVE | THREADED | NB15 | Sea water |  | 3.5 |  |  | 36 |  |  | 39.3231
16 | SP40-01-03-002 | 65-40-SS-SW-05 | MOV-101 | MED-1st effect | MOTORIZED GLOBE VALVE | FLANGED | NB65 | Sea water |  | 3.5 |  |  | 36 |  |  | 13.1077
17 | SP40-01-03-002 | 65-40-SS-SW-06 | MOV-102 | MED-2nd effect | MOTORIZED GLOBE VALVE | FLANGED | NB65 | Sea water |  | 3.5 |  |  | 36 |  |  | 13.1077
18 | SP40-01-03-002 | 65-40-SS-SW-07 | MOV-103 | MED-3rd effect | MOTORIZED GLOBE VALVE | FLANGED | NB65 | Sea water |  | 3.5 |  |  | 36 |  |  | 13.1077
19 | SP40-01-03-001 | 100-40-SS-SW-09 | IV-107 | PIT-104 | BALL VALVE | THREADED | NB15 | Sea water |  | 3.5 |  |  | 36.45 |  |  | 34.723
20 | SP40-01-03-002 | 65-40-SS-SW-10 | MOV-104 | MED-4th effect | MOTORIZED GLOBE VALVE | FLANGED | NB65 | Sea water |  | 3.5 |  |  | 36.45 |  |  | 11.5743
21 | SP40-01-03-002 | 65-40-SS-SW-11 | MOV-105 | MED-5th effect | MOTORIZED GLOBE VALVE | FLANGED | NB65 | Sea water |  | 3.5 |  |  | 36.45 |  |  | 11.5743
22 | SP40-01-03-002 | 65-40-SS-SW-12 | MOV-106 | MED-6th effect | MOTORIZED GLOBE VALVE | FLANGED | NB65 | Sea water |  | 3.5 |  |  | 36.45 |  |  | 11.5743
23 | SP40-01-03-001 | 100-40-SS-SW-14 | IV-108 | PIT-105 | BALL VALVE | THREADED | NB15 | Sea water |  | 3.5 |  |  | 33.9094 |  |  | 38.5811
24 | SP40-01-03-002 | 65-40-SS-SW-15 | MOV-107 | MED-7th effect | MOTORIZED GLOBE VALVE | FLANGED | NB65 | Sea water |  | 3.5 |  |  | 33.9094 |  |  | 12.8604
25 | SP40-01-03-002 | 65-40-SS-SW-16 | MOV-108 | MED-8th effect | MOTORIZED GLOBE VALVE | FLANGED | NB65 | Sea water |  | 3.5 |  |  | 33.9094 |  |  | 12.8604
26 | SP40-01-03-002 | 65-40-SS-SW-17 | MOV-109 | MED-9th effect | MOTORIZED GLOBE VALVE | FLANGED | NB65 | Sea water |  | 3.5 |  |  | 33.9094 |  |  | 12.8604
27 | SP40-01-03-002 | MED - E1 | IV-211 | LT-201 | BALL VALVE | FLANGED | NB25 | Brine |  | 0.32046 |  |  | 70.6
28 | SP40-01-03-002 | MED - E1 | IV-212 | LT-201 | BALL VALVE | FLANGED | NB25 | Brine |  | 0.32046 |  |  | 70.6
29 | SP40-01-03-002 | MED - E1 | DV-209 | LT-201 | BALL VALVE | THREADED | NB15 | Brine |  | 0.32046 |  |  | 70.6
30 | SP40-01-03-002 | MED - E1 | VV-201 | LT-201 | BALL VALVE | THREADED | NB15 | Brine |  | 0.32046 |  |  | 70.6
31 | SP40-01-03-002 | 150-40-SS-BW-01 | DV-201 | Brine siphon - Effect 1 to Effect 2 | BALL VALVE | FLANGED | NB15 | Brine |  | 0 |  |  | 66.55 |  |  | 14.0404
32 | SP40-01-03-002 | 200-40-SS-BW-02 | DV-202 | Brine siphon - Effect 2 to Effect 3 | BALL VALVE | FLANGED | NB15 | Brine |  | 0 |  |  | 62.81 |  |  | 28.7646
33 | SP40-01-03-002 | 250-40-SS-BW-03 | DV-203 | Brine siphon - Effect 3 to Effect 4 | BALL VALVE | FLANGED | NB15 | Brine |  | 0 |  |  | 59.4 |  |  | 43.993
34 | SP40-01-03-002 | 300-40-SS-BW-04 | DV-204 | Brine siphon - Effect 4 to Effect 5 | BALL VALVE | FLANGED | NB15 | Brine |  | 0 |  |  | 56.2 |  |  | 59.6595
35 | SP40-01-03-002 | 350-40-SS-BW-05 | DV-205 | Brine siphon - Effect 5 to Effect 6 | BALL VALVE | FLANGED | NB15 | Brine |  | 0 |  |  | 53.1 |  |  | 75.3968
36 | SP40-01-03-002 | 400-40-SS-BW-06 | DV-206 | Brine siphon - Effect 6 to Effect 7 | BALL VALVE | FLANGED | NB15 | Brine |  | 0 |  |  | 50 |  |  | 91.0631
37 | SP40-01-03-002 | 400-40-SS-BW-07 | DV-207 | Brine siphon - Effect 7 to Effect 8 | BALL VALVE | FLANGED | NB15 | Brine |  | 0 |  |  | 46.72 |  |  | 107.2573
38 | SP40-01-03-002 | 450-40-SS-BW-08 | DV-208 | Brine siphon - Effect 8 to Effect 9 | BALL VALVE | FLANGED | NB15 | Brine |  | 0 |  |  | 43.14 |  |  | 122.9123
39 | SP40-01-03-001 | BT | DV-210 | Brine tank - Drain | BALL VALVE | FLANGED | NB15 | Brine |  | 0.068 |  |  | 39
40 | SP40-01-03-001 | BT | DV-211 | LIT-202 - Drain | BALL VALVE | THREADED | NB15 | Brine |  | 0.068 |  |  | 39
41 | SP40-01-03-001 | BT | IV-213 | LIT-202 - Isolation valve | BALL VALVE | FLANGED | NB25 | Brine |  | 0.068 |  |  | 39
42 | SP40-01-03-001 | BT | IV-214 | LIT-202 - Isolation valve | BALL VALVE | FLANGED | NB25 | Brine |  | 0.068 |  |  | 39
43 | SP40-01-03-001 | ID800-8THK-SS-BW-10 | BFV-201 | Isolation valve | BUTTERFLY VALVE | FLANGED | ID800 | Brine |  | 2.5 |  |  | 39.071 |  |  | 137.9218
44 | SP40-01-03-001 | ID800-8THK-SS-BW-10 | BFV-202 | Isolation valve | BUTTERFLY VALVE | FLANGED | ID800 | Brine |  | 2.5 |  |  | 39.071 |  |  | 137.9218
45 | SP40-01-03-001 | ID800-8THK-SS-BW-10 | DV-212 | ST-201 Drain valve | BALL VALVE | FLANGED | NB15 | Brine |  | 2.5 |  |  | 39.071 |  |  | 137.9218
46 | SP40-01-03-001 | ID800-8THK-SS-BW-10 | DV-213 | ST-202 Drain valve | BALL VALVE | FLANGED | NB16 | Brine |  | 2.5 |  |  | 39.071 |  |  | 137.9218
47 | SP40-01-03-001 | XX-XX-SS-BW-11 | IV-215 | PG-201 - Isolation valve | BALL VALVE | THREADED | NB16 | Brine |  | 2.5 |  |  | 37.4474
48 | SP40-01-03-001 | XX-XX-SS-BW-11 | IV-216 | PG-202 - Isolation valve | BALL VALVE | THREADED | NB16 | Brine |  | 2.5 |  |  | 37.4474
49 | SP40-01-03-001 | XX-XX-SS-BW-11 | NRV-210 | BP SKID - Discharge side | NON RETURN VALVE | FLANGED | HOLD | Brine |  | 2.5 |  |  | 37.4474
50 | SP40-01-03-001 | XX-XX-SS-BW-11 | NRV-211 | BP SKID - Discharge side | NON RETURN VALVE | FLANGED | HOLD | Brine |  | 2.5 |  |  | 37.4474
51 | SP40-01-03-001 | XX-XX-SS-BW-11 | BV-201 | BP SKID - Discharge side | BALL VALVE | FLANGED | HOLD | Brine |  | 2.5 |  |  | 37.4474
52 | SP40-01-03-001 | XX-XX-SS-BW-11 | BV-202 | BP SKID - Discharge side | BALL VALVE | FLANGED | HOLD | Brine |  | 2.5 |  |  | 37.4474
53 | SP40-01-03-001 | XX-XX-SS-BW-11 | IV-217 | PSL-201 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474
54 | SP40-01-03-001 | XX-XX-SS-BW-11 | IV-218 | PIT-211 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474
55 | SP40-01-03-002 | 200-40-SS-BW-12 | IV-219 | PIT-212 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474
56 | SP40-01-03-001 | 200-40-SS-BW-12 | IV-220 | CIT-201 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474
57 | SP40-01-03-002 | 200-40-SS-BW-12 | MOV-210 |  | MOTORIZED GLOBE VALVE | FLANGED | NB200 | Brine |  | 2.5 |  |  | 37.4474
58 | SP40-01-03-002 | 150-40-SS-BW-14 | IV-210 | PIT-210 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 65.4871
59 | SP40-01-03-002 | 80-40-SS-BW-15 | NRV-201 | Brine make-up line MED - Effect 1 | NON RETURN VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 6.367
60 | SP40-01-03-002 | 80-40-SS-BW-15 | IV-201 | PIT-201 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 6.367
61 | SP40-01-03-002 | 80-40-SS-BW-15 | BV-203 | Brine make-up line MED - Effect 1 | BALL VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 6.367
62 | SP40-01-03-002 | 80-40-SS-BW-16 | NRV-202 | Brine make-up line MED - Effect 2 | NON RETURN VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 6.367
63 | SP40-01-03-002 | 80-40-SS-BW-16 | IV-202 | PIT-202 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 6.367
64 | SP40-01-03-002 | 80-40-SS-BW-16 | BV-204 | Brine make-up line MED - Effect 2 | BALL VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 6.367
65 | SP40-01-03-002 | 80-40-SS-BW-17 | NRV-203 | Brine make-up line MED - Effect 3 | NON RETURN VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 6.3324
66 | SP40-01-03-002 | 80-40-SS-BW-17 | IV-203 | PIT-203 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 6.3324
67 | SP40-01-03-002 | 80-40-SS-BW-17 | BV-205 | Brine make-up line MED - Effect 3 | BALL VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 6.3324
68 | SP40-01-03-002 | 80-40-SS-BW-18 | NRV-204 | Brine make-up line MED - Effect 4 | NON RETURN VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.9934
69 | SP40-01-03-002 | 80-40-SS-BW-18 | IV-204 | PIT-204 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.9934
70 | SP40-01-03-002 | 80-40-SS-BW-18 | BV-206 | Brine make-up line MED - Effect 4 | BALL VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.9934
71 | SP40-01-03-002 | 80-40-SS-BW-19 | NRV-205 | Brine make-up line MED - Effect 5 | NON RETURN VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.9934
72 | SP40-01-03-002 | 80-40-SS-BW-19 | IV-205 | PIT-205 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.9934
73 | SP40-01-03-002 | 80-40-SS-BW-19 | BV-207 | Brine make-up line MED - Effect 5 | BALL VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.9934
74 | SP40-01-03-002 | 80-40-SS-BW-20 | NRV-206 | Brine make-up line MED - Effect 6 | NON RETURN VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.9934
75 | SP40-01-03-002 | 80-40-SS-BW-20 | IV-206 | PIT-206 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.9934
76 | SP40-01-03-002 | 80-40-SS-BW-20 | BV-208 | Brine make-up line MED - Effect 6 | BALL VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.9934
77 | SP40-01-03-002 | 80-40-SS-BW-21 | NRV-207 | Brine make-up line MED - Effect 7 | NON RETURN VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.4744
78 | SP40-01-03-002 | 80-40-SS-BW-21 | IV-207 | PIT-207 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.4744
79 | SP40-01-03-002 | 80-40-SS-BW-21 | BV-209 | Brine make-up line MED - Effect 7 | BALL VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.4744
80 | SP40-01-03-002 | 80-40-SS-BW-22 | NRV-208 | Brine make-up line MED - Effect 8 | NON RETURN VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.4744
81 | SP40-01-03-002 | 80-40-SS-BW-22 | IV-208 | PIT-208 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.4744
82 | SP40-01-03-002 | 80-40-SS-BW-22 | BV-210 | Brine make-up line MED - Effect 8 | BALL VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.4744
83 | SP40-01-03-002 | 80-40-SS-BW-23 | NRV-209 | Brine make-up line MED - Effect 9 | NON RETURN VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.4744
84 | SP40-01-03-002 | 80-40-SS-BW-23 | IV-209 | PIT-209 | BALL VALVE | THREADED | NB15 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.4744
85 | SP40-01-03-002 | 80-40-SS-BW-23 | BV-211 | Brine make-up line MED - Effect 9 | BALL VALVE | FLANGED | NB80 | Brine |  | 2.5 |  |  | 37.4474 |  |  | 7.4744
86 | SP40-01-03-002 | MED - E1 | DV-301 | Vapour box - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.32046 |  |  | 70.6
87 | SP40-01-03-002 | MED - E1 | IV-301 | LIT-301 | BALL VALVE | FLANGED | NB25 | Distillate |  | 0.32046 |  |  | 70.6
88 | SP40-01-03-002 | MED - E1 | IV-302 | LIT-301 | BALL VALVE | FLANGED | NB25 | Distillate |  | 0.32046 |  |  | 70.6
89 | SP40-01-03-002 | MED - E1 | DV-302 | LIT-301 - Drain | BALL VALVE | THREADED | NB15 | Distillate |  | 0.32046 |  |  | 70.6
90 | SP40-01-03-002 | MED - E1 | VV-301 | LIT-301 - Vent | BALL VALVE | THREADED | NB15 | Distillate |  | 0.32046 |  |  | 70.6
91 | SP40-01-03-002 | 100-40-SS-DW-01 | DV-303 | Distillate Siphon - Effect 1 outlet to effect 2 inlet | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 70.59 |  |  | 6.85
92 | SP40-01-03-002 | MED - E2 | DV-304 | Vapour box - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.2594 |  |  | 66.55
93 | SP40-01-03-002 | 150-40-SS-DW-02 | DV-305 | Distillate Siphon - Effect 2 outlet to effect 3 inlet | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 65.74 |  |  | 12.2945
94 | SP40-01-03-002 | MED - E3 | DV-306 | Vapour box - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.2196 |  |  | 62.81
95 | SP40-01-03-002 | 150-40-SS-DW-03 | DV-307 | Distillate Siphon - Effect 3outlet to effect 4 inlet | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 62.02 |  |  | 17.0025
96 | SP40-01-03-002 | MED - E3 | DV-308 |  | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.2196 |  |  | 62.81
97 | SP40-01-03-002 | MED - E4 | DV-309 | Vapour box - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.188 |  |  | 59.4
98 | SP40-01-03-002 | 200-40-SS-DW-04 | DV-310 | Distillate Siphon - Effect 4 outlet to effect 5 inlet | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 58.62 |  |  | 21.1947
99 | SP40-01-03-002 | MED - E5 | DV-311 | Vapour box - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.1618 |  |  | 56.2
100 | SP40-01-03-002 | 200-40-SS-DW-05 | DV-312 | Distillate Siphon - Effect 5 outlet to effect 6 inlet | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 55.43 |  |  | 25.1275
101 | SP40-01-03-002 | MED - E6 | DV-313 | Vapour box - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.1395 |  |  | 53.1
102 | SP40-01-03-002 | 200-40-SS-DW-06 | DV-314 | Distillate Siphon - Effect 6 outlet to effect 7 inlet | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 52.33 |  |  | 28.9103
103 | SP40-01-03-002 | MED - E6 | DV-315 |  | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.1395 |  |  | 53.1
104 | SP40-01-03-002 | MED - E7 | DV-316 | Vapour box - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.1198 |  |  | 50
105 | SP40-01-03-002 | 200-40-SS-DW-07 | DV-317 | Distillate Siphon - Effect 7 outlet to effect 8 inlet | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 49.23 |  |  | 32.7972
106 | SP40-01-03-002 | MED - E8 | DV-318 | Vapour box - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.1017 |  |  | 46.72
107 | SP40-01-03-002 | 250-40-SS-DW-08 | DV-319 | Distillate Siphon - Effect 8 outlet to effect 9 inlet | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 45.97 |  |  | 36.9316
108 | SP40-01-03-002 | MED - E9 | DV-320 | Vapour box - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.0846 |  |  | 43.14
109 | SP40-01-03-002 | 450-40-SS-DW-09 | DV-321 | Distillate Siphon - Effect 9 outlet to distillate tank inlet | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 42.4045 |  |  | 41.6016
110 | SP40-01-03-001 | DT | DV-322 | Distillate tank - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0.0846 |  |  | 42.4045
111 | SP40-01-03-001 | DT | DV-323 | LIT-302 - Drain | BALL VALVE | THREADED | NB15 | Distillate |  | 0.0846 |  |  | 42.4045
112 | SP40-01-03-001 | DT | IV-303 | LIT-302 - Isolation valve | BALL VALVE | FLANGED | NB25 | Distillate |  | 0.0846 |  |  | 42.4045
113 | SP40-01-03-001 | DT | IV-304 | LIT-302 - Isolation valve | BALL VALVE | FLANGED | NB25 | Distillate |  | 0.0846 |  |  | 42.4045
114 | SP40-01-03-001 | 450-40-SS-DW-10 | BFV-301 | Isolation valve | BUTTERFLY VALVE | FLANGED | ID800 | Distillate |  | 1.5 |  |  | 42.4936 |  |  | 42.0524
115 | SP40-01-03-001 | 450-40-SS-DW-10 | BFV-302 | Isolation valve | BUTTERFLY VALVE | FLANGED | ID800 | Distillate |  | 1.5 |  |  | 42.4936 |  |  | 42.0524
116 | SP40-01-03-001 | 450-40-SS-DW-10 | DV-324 | ST-301 Drain valve | BALL VALVE | FLANGED | NB15 | Distillate |  | 1.5 |  |  | 42.4936 |  |  | 42.0524
117 | SP40-01-03-001 | 450-40-SS-DW-10 | DV-325 | ST-302 Drain valve | BALL VALVE | FLANGED | NB16 | Distillate |  | 1.5 |  |  | 42.4936 |  |  | 42.0524
118 | SP40-01-03-001 | 100-40-SS-DW-11 | IV-305 | PG-301 - Isolation valve | BALL VALVE | THREADED | NB16 | Distillate |  | 0 |  |  | 42.4936 |  |  | 42.0524
119 | SP40-01-03-001 | 100-40-SS-DW-11 | IV-306 | PG-302 - Isolation valve | BALL VALVE | THREADED | NB16 | Distillate |  | 0 |  |  | 42.4936 |  |  | 42.0524
120 | SP40-01-03-001 | 100-40-SS-DW-11 | NRV-301 | DP SKID - Discharge side | NON RETURN VALVE | FLANGED | NB100 | Distillate |  | 0 |  |  | 42.4936 |  |  | 42.0524
121 | SP40-01-03-001 | 100-40-SS-DW-11 | NRV-302 | DP SKID - Discharge side | NON RETURN VALVE | FLANGED | NB100 | Distillate |  | 0 |  |  | 42.4936 |  |  | 42.0524
122 | SP40-01-03-001 | 100-40-SS-DW-11 | BV-301 | DP SKID - Discharge side | BALL VALVE | FLANGED | NB100 | Distillate |  | 0 |  |  | 42.4936 |  |  | 42.0524
123 | SP40-01-03-001 | 100-40-SS-DW-11 | BV-302 | DP SKID - Discharge side | BALL VALVE | FLANGED | NB100 | Distillate |  | 0 |  |  | 42.4936 |  |  | 42.0524
124 | SP40-01-03-001 | 100-40-SS-DW-11 | IV-307 | PSL-301 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 42.4936 |  |  | 42.0524
125 | SP40-01-03-001 | 100-40-SS-DW-11 | IV-308 | PIT-301 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 42.4936 |  |  | 42.0524
126 | SP40-01-03-001 | 100-40-SS-DW-12 | IV-309 | CIT-301 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 0 |  |  | 42.0524
127 | SP40-01-03-001 | 100-40-SS-DW-12 | MOV-301 |  | MOTORIZED GLOBE VALVE | FLANGED | NB100 | Distillate |  | 0 |  |  | 0 |  |  | 42.0524
128 | SP40-01-03-001 | 100-40-SS-DW-14 | NRV-303 |  | NON RETURN VALVE | FLANGED | NB100 | Distillate |  | 0 |  |  | 0 |  |  | 42.0524
129 | SP40-01-03-003 | DST | IV-310 | LIT-301 | BALL VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 0
130 | SP40-01-03-003 | DST | IV-311 | LIT-301 | BALL VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 0
131 | SP40-01-03-003 | DST | DV-326 | LIT-301 - Drain | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 0
132 | SP40-01-03-003 | DST | VV-304 | LIT-301 - Vent | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 0
133 | SP40-01-03-003 | DST | DV-327 | Distillate tank - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 0
134 | SP40-01-03-003 | 100-40-SS-DW-15 | BFV-303 | IFP - Suction | BUTTERFLY VALVE | FLANGED | NB100 | Distillate |  | 0 |  |  | 30 |  |  | 2.2084
135 | SP40-01-03-003 | 100-40-SS-DW-15 | DV-328 | ST-303 - Drain | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 30 |  |  | 2.2084
136 | SP40-01-03-003 | 100-40-SS-DW-15 | IV-312 | IFP - Discharge | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 30 |  |  | 2.2084
137 | SP40-01-03-003 | 100-40-SS-DW-15 | NRV-304 | IFP - Discharge | NON RETURN VALVE | FLANGED | NB100 | Distillate |  | 0 |  |  | 30 |  |  | 2.2084
138 | SP40-01-03-003 | 100-40-SS-DW-17 | BV-303 | IFP - Discharge | BALL VALVE | FLANGED | NB100 | Distillate |  | 0 |  |  | 30 |  |  | 2.2084
139 | SP40-01-03-003 | 100-40-SS-DW-18 | BV-304 | IFP - Discharge | BALL VALVE | FLANGED | NB100 | Distillate |  | 0 |  |  | 30 |  |  | 2.2084
140 | SP40-01-03-003 | 25-40-SS-DW-19 | BFV-304 | MP-1 Suction | BUTTERFLY VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
141 | SP40-01-03-003 | 25-40-SS-DW-19 | BFV-305 | MP-2 Suction | BUTTERFLY VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
142 | SP40-01-03-003 | 25-40-SS-DW-19 | DV-329 | ST-304 | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
143 | SP40-01-03-003 | 25-40-SS-DW-19 | DV-330 | ST-305 | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
144 | SP40-01-03-003 | 25-40-SS-DW-20 | IV-313 | PG-304 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
145 | SP40-01-03-003 | 25-40-SS-DW-20 | IV-314 | PG-305 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
146 | SP40-01-03-003 | 25-40-SS-DW-20 | NRV-305 |  | NON RETURN VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
147 | SP40-01-03-003 | 25-40-SS-DW-20 | NRV-306 |  | NON RETURN VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
148 | SP40-01-03-003 | 25-40-SS-DW-20 | BV-305 |  | BALL VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
149 | SP40-01-03-003 | 25-40-SS-DW-20 | BV-306 |  | BALL VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
150 | SP40-01-03-003 | 25-40-SS-DW-20 | IV-315 | PSL-302 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
151 | SP40-01-03-003 | 25-40-SS-DW-20 | IV-316 | PIT-302 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
152 | SP40-01-03-003 | 25-40-SS-DW-21 | PRV-301 |  | PRESSURE RETAINING VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
153 | SP40-01-03-003 | 25-40-SS-DW-22 | BV-307 | BEFORE MOV-302 | BALL VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
154 | SP40-01-03-003 | 25-40-SS-DW-22 | MOV-302 |  | MOTORIZED GLOBE VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 30 |  |  | 0.14495
155 | SP40-01-03-003 | LTFV | IV-317 | LT-304 | BALL VALVE | FLANGED | NB25 | Distillate |  | 0.067969 |  |  | 38.3888
156 | SP40-01-03-003 | LTFV | IV-318 | LT-304 | BALL VALVE | FLANGED | NB25 | Distillate |  | 0.067969 |  |  | 38.3888
157 | SP40-01-03-003 | LTFV | DV-331 | LT-304 - Drain | BALL VALVE | THREADED | NB15 | Distillate |  | 0.067969 |  |  | 38.3888
158 | SP40-01-03-003 | LTFV | VV-305 | LT-304 - Vent | BALL VALVE | THREADED | NB15 | Distillate |  | 0.067969 |  |  | 38.3888
159 | SP40-01-03-003 | 300-40-SS-DW-23 | BFV-306 | LTFV-RCP-1 Suction | BUTTERFLY VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
160 | SP40-01-03-003 | 300-40-SS-DW-23 | BFV-307 | LTFV-RCP-2 Suction | BUTTERFLY VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
161 | SP40-01-03-003 | 300-40-SS-DW-23 | DV-332 | ST-306 | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
162 | SP40-01-03-003 | 300-40-SS-DW-23 | DV-333 | ST-307 | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
163 | SP40-01-03-003 | 80-40-SS-DW-24 | IV-321 | PG-306 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
164 | SP40-01-03-003 | 80-40-SS-DW-24 | IV-322 | PG-307 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
165 | SP40-01-03-003 | 80-40-SS-DW-24 | NRV-307 | LTFV-RCP-1 Delivery | NON RETURN VALVE | FLANGED | NB80 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
166 | SP40-01-03-003 | 80-40-SS-DW-24 | NRV-308 | LTFV-RCP-2 Delivery | NON RETURN VALVE | FLANGED | NB80 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
167 | SP40-01-03-003 | 80-40-SS-DW-24 | BV-310 | LTFV-RCP-1 Delivery | BALL VALVE | FLANGED | NB80 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
168 | SP40-01-03-003 | 80-40-SS-DW-24 | BV-311 | LTFV-RCP-2 Delivery | BALL VALVE | FLANGED | NB80 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
169 | SP40-01-03-003 | 80-40-SS-DW-24 | IV-323 | PSL-303 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
170 | SP40-01-03-003 | 80-40-SS-DW-24 | IV-324 | PIT-303 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 38.39 |  |  | 21.6101
171 | SP40-01-03-003 | 15-40-SS-DW-26 | BV-308 | Before MOV-303 | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 70 |  |  | 11.2716
172 | SP40-01-03-003 | 15-40-SS-DW-26 | MOV-303 |  | MOTORIZED GLOBE VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 70 |  |  | 11.2716
173 | SP40-01-03-003 | HTFV | IV-319 | LT-305 | BALL VALVE | FLANGED | NB25 | Distillate |  | 0.32046 |  |  | 70.6
174 | SP40-01-03-003 | HTFV | IV-320 | LT-305 | BALL VALVE | FLANGED | NB25 | Distillate |  | 0.32046 |  |  | 70.6
175 | SP40-01-03-003 | HTFV | DV-334 | LT-305 - Drain | BALL VALVE | THREADED | NB15 | Distillate |  | 0.32046 |  |  | 70.6
176 | SP40-01-03-003 | HTFV | VV-306 | LT-305 - Vent | BALL VALVE | THREADED | NB15 | Distillate |  | 0.32046 |  |  | 70.6
177 | SP40-01-03-003 | 200-40-SS-DW-28 | BFV-306 | HTFV-RCP-1 Suction | BUTTERFLY VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 69.56
178 | SP40-01-03-003 | 200-40-SS-DW-28 | BFV-307 | HTFV-RCP-2 Suction | BUTTERFLY VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 69.56
179 | SP40-01-03-003 | 200-40-SS-DW-28 | DV-332 | ST-306 | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 69.56
180 | SP40-01-03-003 | 200-40-SS-DW-28 | DV-333 | ST-307 | BALL VALVE | FLANGED | NB15 | Distillate |  | 0 |  |  | 69.56
181 | SP40-01-03-003 | 50-40-SS-DW-29 | IV-325 | PG-306 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 69.56
182 | SP40-01-03-003 | 50-40-SS-DW-29 | IV-326 | PG-307 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 69.56
183 | SP40-01-03-003 | 50-40-SS-DW-29 | NRV-309 | HTFV-RCP-1 Delivery | NON RETURN VALVE | FLANGED | NB50 | Distillate |  | 0 |  |  | 69.56
184 | SP40-01-03-003 | 50-40-SS-DW-29 | NRV-310 | HTFV-RCP-2 Delivery | NON RETURN VALVE | FLANGED | NB50 | Distillate |  | 0 |  |  | 69.56
185 | SP40-01-03-003 | 50-40-SS-DW-29 | BV-312 | HTFV-RCP-1 Delivery | BALL VALVE | FLANGED | NB50 | Distillate |  | 0 |  |  | 69.56
186 | SP40-01-03-003 | 50-40-SS-DW-29 | BV-313 | HTFV-RCP-2 Delivery | BALL VALVE | FLANGED | NB50 | Distillate |  | 0 |  |  | 69.56
187 | SP40-01-03-003 | 50-40-SS-DW-29 | IV-327 | PSL-304 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 69.56
188 | SP40-01-03-003 | 50-40-SS-DW-29 | IV-328 | PIT-304 | BALL VALVE | THREADED | NB15 | Distillate |  | 0 |  |  | 69.56
189 | SP40-01-03-003 | 25-40-SS-DW-31 | BV-309 | Before De-Super heater | BALL VALVE | FLANGED | NB25 | Distillate |  | 0 |  |  | 30 |  |  | 0.50601
190 | SP40-01-03-003 | LTFV | IV-401 | Low Temperature Flash Vessel - PIT 401 | BALL VALVE | THREADED | NB15 | Steam |  | 0.067969 |  |  | 38.3888
191 | SP40-01-03-002 | XXX-40-SS-ST-10 | IV-403 | MVC-1 Discharge Side - PIT 403 | BALL VALVE | THREADED | NB15 | Steam |  | 0 |  |  | 0
192 | SP40-01-03-002 | XXX-40-SS-ST-11 | IV-404 | MVC-2 Discharge Side - PIT 404 | BALL VALVE | THREADED | NB15 | Steam |  | 0 |  |  | 0
193 | SP40-01-03-002 | XXX-40-SS-ST-12 | IV-405 | MVC-3 Discharge Side - PIT 405 | BALL VALVE | THREADED | NB15 | Steam |  | 0 |  |  | 0
194 | SP40-01-03-002 | MED - E1 | IV-407 | MED 1st Effect Vapour Box - PIT 407 | BALL VALVE | THREADED | NB15 | Steam |  | 0.32046 |  |  | 70.6
195 | SP40-01-03-002 | MED - E1 | IV-408 | MED 1st Effect - PIT 408 | BALL VALVE | THREADED | NB15 | Steam |  | 0.32046 |  |  | 70.6
196 | SP40-01-03-002 | MED - E2 | IV-409 | MED 2nd Effect - PIT 409 | BALL VALVE | THREADED | NB15 | Steam |  | 0.2594 |  |  | 66.55
197 | SP40-01-03-002 | MED - E3 | IV-410 | MED 3rd Effect - PIT 410 | BALL VALVE | THREADED | NB15 | Steam |  | 0.2196 |  |  | 62.81
198 | SP40-01-03-002 | MED - E4 | IV-411 | MED 4th Effect - PIT 411 | BALL VALVE | THREADED | NB15 | Steam |  | 0.188 |  |  | 59.4
199 | SP40-01-03-002 | MED - E5 | IV-412 | MED 5th Effect - PIT 412 | BALL VALVE | THREADED | NB15 | Steam |  | 0.1618 |  |  | 56.2
200 | SP40-01-03-002 | MED - E6 | IV-413 | MED 6th Effect - PIT 413 | BALL VALVE | THREADED | NB15 | Steam |  | 0.1395 |  |  | 53.1
201 | SP40-01-03-002 | MED - E7 | IV-414 | MED 7th Effect - PIT 414 | BALL VALVE | THREADED | NB15 | Steam |  | 0.1198 |  |  | 50
202 | SP40-01-03-002 | MED - E8 | IV-415 | MED 8th Effect - PIT 415 | BALL VALVE | THREADED | NB15 | Steam |  | 0.1017 |  |  | 46.72
203 | SP40-01-03-002 | MED - E9 | IV-416 | MED 9th Effect - PIT 416 | BALL VALVE | THREADED | NB15 | Steam |  | 0.0846 |  |  | 43.14
204 | SP40-01-03-002 | MED - E9 | IV-417 | MED 9th Effect - PIT 417 | BALL VALVE | THREADED | NB15 | Steam |  | 0.0846 |  |  | 43.14
205 | SP40-01-03-003 | HTFV | IV-406 | High Temperature Flash Vessel - PIT 406 | BALL VALVE | THREADED | NB15 | Steam |  | 0.32046 |  |  | 70.6
206 | SP40-01-03-002 | ID1100-THK-SS-ST-09 | IV-402 | MVC-1 Suction Side - PIT 402 | BALL VALVE | THREADED | NB15 | Steam |  | 0 |  |  | 39 |  |  | 140279.5426
207 | SP40-01-03-002 | 40-40-SS-NCG-01 | BV-501 | MED 1st Effect to 2nd Effect | BALL VALVE | FLANGED | NB40 | NCG |  | 0 |  |  | 36.5 |  |  | 1.3819
208 | SP40-01-03-002 | 40-40-SS-NCG-02 | BV-502 | MED 2nd Effect to 3rd Effect | BALL VALVE | FLANGED | NB40 | NCG |  | 0 |  |  | 36.5 |  |  | 3.5575
209 | SP40-01-03-002 | 40-40-SS-NCG-03 | BV-503 | MED 3rd Effect to 4th Effect | BALL VALVE | FLANGED | NB40 | NCG |  | 0 |  |  | 36.5 |  |  | 6.7509
210 | SP40-01-03-002 | 50-40-SS-NCG-04 | BV-504 | MED 4th Effect to 5th Effect | BALL VALVE | FLANGED | NB50 | NCG |  | 0 |  |  | 36.9 |  |  | 11.121
211 | SP40-01-03-002 | 50-40-SS-NCG-05 | BV-505 | MED 5th Effect to 6th Effect | BALL VALVE | FLANGED | NB50 | NCG |  | 0 |  |  | 36.9 |  |  | 17.5422
212 | SP40-01-03-002 | 50-40-SS-NCG-06 | BV-506 | MED 6th Effect to 7th Effect | BALL VALVE | FLANGED | NB50 | NCG |  | 0 |  |  | 36.9 |  |  | 27.3316
213 | SP40-01-03-002 | 50-40-SS-NCG-07 | BV-507 | MED 7th Effect to 8th Effect | BALL VALVE | FLANGED | NB50 | NCG |  | 0 |  |  | 35.7 |  |  | 39.5833
214 | SP40-01-03-002 | 100-40-SS-NCG-08 | BV-508 | MED 8th Effect to 9th Effect | BALL VALVE | FLANGED | NB100 | NCG |  | 0 |  |  | 44.01 |  |  | 287.7176
215 | SP40-01-03-002 | 200-40-SS-NCG-09 | BV-509 | MED 9th Effect to Final Condenser | BALL VALVE | FLANGED | NB200 | NCG |  | 0 |  |  | 41.91 |  |  | 2091.5728
216 | SP40-01-03-001 | FC | IV-501 | Final Condenser - PIT 501 | BALL VALVE | THREADED | NB15 | NCG |  | 0.082 |  |  | 41.91
217 | SP40-01-03-001 | XX-40-SS-NCG-10 | IV-502 | LRVP-1&2 Pump Suction Side - PIT | BALL VALVE | THREADED | NB15 | NCG |  | 0 |  |  | 0
218 | SP40-01-03-001 | XX-40-SS-NCG-10 | BV-510 | LRVP-1 Pump Suction Side | BALL VALVE | FLANGED | NB100 | NCG |  | 0 |  |  | 0
219 | SP40-01-03-001 | XX-40-SS-NCG-10 | BV-511 | LRVP-2 Pump Suction Side | BALL VALVE | FLANGED | NB100 | NCG |  | 0 |  |  | 0
220 | SP40-01-03-001 | XX-40-SS-NCG-11 | IV-503 | LRVP-1 Pump Discharge Side - PIT 503 | BALL VALVE | THREADED | NB15 | NCG |  | 0 |  |  | 0
221 | SP40-01-03-001 | XX-40-SS-NCG-11 | IV-504 | LRVP-2 Pump Discharge Side - PIT 504 | BALL VALVE | THREADED | NB15 | NCG |  | 0 |  |  | 0
222 | SP40-01-03-001 | XX-40-SS-NCG-11 | NRV-501 | LRVP-1 Pump Discharge Side | NON RETURN VALVE | FLANGED | NB100 | NCG |  | 0 |  |  | 0
223 | SP40-01-03-001 | XX-40-SS-NCG-11 | NRV-502 | LRVP-2 Pump Discharge Side | NON RETURN VALVE | FLANGED | NB100 | NCG |  | 0 |  |  | 0
224 | SP40-01-03-001 | XX-40-SS-NCG-11 | BV-512 | LRVP-1 Pump Discharge Side | BALL VALVE | FLANGED | NB100 | NCG |  | 0 |  |  | 0
225 | SP40-01-03-001 | XX-40-SS-NCG-11 | BV-513 | LRVP-2 Pump Discharge Side | BALL VALVE | FLANGED | NB100 | NCG |  | 0 |  |  | 0
226 | SP40-01-03-004 | AST | DV-601 | Anti-Scalant Tank- Drain | BALL VALVE | FLANGED | HOLD | Dosing |  | 0 |  |  | 0
227 | SP40-01-03-004 | AST | VV-805 | Anti-Scalant Tank- Vent | BALL VALVE | FLANGED | HOLD | Dosing |  | 0 |  |  | 0
228 | SP40-01-03-004 | AFT | DV-602 | Anti-Form Tank- Drain | BALL VALVE | FLANGED | HOLD | Dosing |  | 0 |  |  | 0
229 | SP40-01-03-004 | AFT | VV-806 | Anti-Form Tank- Vent | BALL VALVE | FLANGED | HOLD | Dosing |  | 0 |  |  | 0
230 | SP40-01-03-004 | ACT | DV-603 | Acid Cleaning Tank- Drain | BALL VALVE | FLANGED | HOLD | Dosing |  | 0 |  |  | 0
231 | SP40-01-03-004 | ACT | VV-807 | Acid Cleaning Tank- Vent | BALL VALVE | FLANGED | HOLD | Dosing |  | 0 |  |  | 0
232 | SP40-01-03-004 | XX-40-SS-DO-01 | NRV-601 | AST Pump Discharge Side | NON RETURN VALVE | FLANGED | HOLD | Dosing |  | #N/A |  |  | #N/A
233 | SP40-01-03-004 | XX-40-SS-DO-01 | BV-601 | AST Pump Discharge Side | BALL VALVE | FLANGED | HOLD | Dosing |  | #N/A |  |  | #N/A
234 | SP40-01-03-004 | XX-40-SS-DO-02 | NRV-602 | AFT Pump Discharge Side | NON RETURN VALVE | FLANGED | HOLD | Dosing |  | #N/A |  |  | #N/A
235 | SP40-01-03-004 | XX-40-SS-DO-02 | BV-602 | AFT Pump Discharge Side | BALL VALVE | FLANGED | HOLD | Dosing |  | #N/A |  |  | #N/A
236 | SP40-01-03-004 | XX-40-SS-DO-03 | NRV-603 | ACT Pump Discharge Side | NON RETURN VALVE | FLANGED | HOLD | Dosing |  | #N/A |  |  | #N/A
237 | SP40-01-03-004 | XX-40-SS-DO-03 | BV-603 | ACT Pump Discharge Side | BALL VALVE | FLANGED | HOLD | Dosing |  | #N/A |  |  | #N/A
238 | SP40-01-03-004 | 50-40-SS-SE-01 | BV-701 | Service Water to Anti-Scalant Tank | BALL VALVE | FLANGED | NB50 | Service water |  | #N/A |  |  | #N/A
239 | SP40-01-03-004 | 50-40-SS-SE-02 | BV-702 | Service Water to Anti-Form Tank | BALL VALVE | FLANGED | NB50 | Service water |  | #N/A |  |  | #N/A
240 | SP40-01-03-004 | 50-40-SS-SE-03 | BV-703 | Service Water to Acid Cleaning Tank | BALL VALVE | FLANGED | NB50 | Service water |  | #N/A |  |  | #N/A
241 | SP40-01-03-001 | 50-40-SS-SE-04 | BV-703 | Service Water to Brine Tank | BALL VALVE | FLANGED | NB50 | Service water |  | #N/A |  |  | #N/A
242 | SP40-01-03-001 | 15-40-SS-VE-01 | VV-801 | Brine tank to 9th effect tube side | BALL VALVE | FLANGED | NB15 | Vent |  | #N/A |  |  | #N/A
243 | SP40-01-03-001 | 15-40-SS-VE-02 | VV-802 | LG-202 to brine tank | BALL VALVE | THREADED | NB15 | Vent |  | #N/A |  |  | #N/A
244 | SP40-01-03-001 | 15-40-SS-VE-03 | VV-803 | Distillate tank to Final Condenser | BALL VALVE | FLANGED | NB15 | Vent |  | #N/A |  |  | #N/A
245 | SP40-01-03-001 | 15-40-SS-VE-04 | VV-804 | LG-302 to distillate tank | BALL VALVE | THREADED | NB15 | Vent |  | #N/A |  |  | #N/A
LIST OF STRAINERS
1 | SP40-01-03-001 | Sea Water Pump Skid | ST-101 | SWP-1 Suction side | Y-STRAINER | FLANGED | NB200 |  |  | #N/A |  |  | #N/A
2 | SP40-01-03-001 | Sea Water Pump Skid | ST-102 | SWP-2 Suction side | Y-STRAINER | FLANGED | NB200 |  |  | #N/A |  |  | #N/A
3 | SP40-01-03-001 | Brine Pump Skid | ST-201 | BP-1 Suction side | Y-STRAINER | FLANGED | ID800 |  |  | #N/A |  |  | #N/A
4 | SP40-01-03-001 | Brine Pump Skid | ST-202 | BP-2 Suction side | Y-STRAINER | FLANGED | ID800 |  |  | #N/A |  |  | #N/A
5 | SP40-01-03-001 | Distillate Pump Skid | ST-301 | DP-1 Suction side | Y-STRAINER | FLANGED | NB450 |  |  | #N/A |  |  | #N/A
6 | SP40-01-03-001 | Distillate Pump Skid | ST-302 | DP-2 Suction side | Y-STRAINER | FLANGED | NB450 |  |  | #N/A |  |  | #N/A
7 | SP40-01-03-003 | Initial Fill Pump | ST-303 | IFP-1 Suction side | Y-STRAINER | FLANGED | NB100 |  |  | #N/A |  |  | #N/A
8 | SP40-01-03-003 | Make-Up Pump Skid | ST-304 | MP-1 Suction side | Y-STRAINER | FLANGED | NB25 |  |  | #N/A |  |  | #N/A
9 | SP40-01-03-003 | Make-Up Pump Skid | ST-305 | MP-2 Suction side | Y-STRAINER | FLANGED | NB25 |  |  | #N/A |  |  | #N/A
10 | SP40-01-03-003 | LTFV - Re-Circulation Pump Skid | ST-306 | LTFV-RCP-1 Suction side | Y-STRAINER | FLANGED | NB300 |  |  | #N/A |  |  | #N/A
11 | SP40-01-03-003 | LTFV - Re-Circulation Pump Skid | ST-307 | LTFV-RCP-2 Suction side | Y-STRAINER | FLANGED | NB300 |  |  | #N/A |  |  | #N/A
12 | SP40-01-03-003 | HTFV - Re-Circulation Pump Skid | ST-308 | HTFV-RCP-1 Suction side | Y-STRAINER | FLANGED | NB200 |  |  | #N/A |  |  | #N/A
13 | SP40-01-03-003 | HTFV - Re-Circulation Pump Skid | ST-309 | HTFV-RCP-2 Suction side | Y-STRAINER | FLANGED | NB200 |  |  | #N/A |  |  | #N/A

## Pipe Table
ID (mm) | ID (mm) | Pipe Size (NB) | OD (mm) | Thickness Sch 40 (mm)
0 | 15.76 | 15 | 21.3 | 2.77
15.76 | 26.64 | 25 | 33.4 | 3.38
26.64 | 40.94 | 40 | 48.3 | 3.68
40.94 | 52.48 | 50 | 60.3 | 3.91
52.48 | 62.68 | 65 | 73 | 5.16
62.68 | 77.92 | 80 | 88.9 | 5.49
77.92 | 102.26 | 100 | 114.3 | 6.02
102.26 | 154.08 | 150 | 168.3 | 7.11
154.08 | 202.74 | 200 | 219.1 | 8.18
202.74 | 254.56 | 250 | 273.1 | 9.27
254.56 | 303.64 | 300 | 323.9 | 10.13
303.64 | 333.34 | 350 | 355.6 | 11.13
333.34 | 381 | 400 | 406.4 | 12.7
381 | 428.6 | 450 | 457 | 14.2
428.6 | 477.82 | 500 | 508 | 15.09
477.82 | 524.04 | 550 | 559 | 17.48
524.04 | 575.04 | 600 | 610 | 17.48
575.04 | Plate | Plate | Plate | Plate

## FluidList (hidden)
SEA WATER
BRINE WATER
DISTILLATE WATER
STEAM
NCG
FEED WATER